## ULC Cover Page
444 William Street, Victoria, BC, V9A 3Y9
Phone: (250) 475-6077
service@cantec.ca
www.cantec.ca
2025
ANNUAL FIRE ALARM SYSTEM INSPECTION & TESTING RECORD
|  | Prepared for: | Concert Realty Services Ltd.
|  | Building Address: | 655 Douglas Street
|  | Building Name: | The Q Apartments
|  | Date: | May 21 - 23, 2025
Please be advised that Cantec Fire Alarms Ltd. is once again an authorized dealer for Mircom. Please don’t hesitate to reach out and inquire about this partnership and what it offers you, our client.
FPABC Cantec Fire Alarms Ltd. is a proud and contributing member to the Fire Protection Association of British Columbia since 2020.
This is to certify that the Alarm Service Company is included by Underwriters Laboratories Inc. (UL) in its Product Directories as eligible to use the UL Listing Mark in connection with Certificated Alarm Systems.
Cantec Fire Alarms will continue its endeavour to exceed industry standards; our annual audit requirements to remain a ULC listed Fire Alarm Service Provider, contributes to this effort. The pages contained within this report are compliant with the standards set by the 2024 BC Fire Code and Part 20 "Annual Fire Alarm System Test and Inspection Record" CAN/ULC S536-19 (Including Revision 1)

## Deficiency Summary
Deficiency Summary for Annual Inspection
NOTE: This page is an addition to the CAN/ULC S536-19 Report to provide a comprehensive overview of all life safety equipment deficiencies.
Attention to: |  | Concert Realty Services Ltd. | Site Name: | The Q Apartments
Date: |  | May 21 - 23, 2025 | Site Address: | 655 Douglas Street
OWNER IS RESPONSIBLE FOR THE FOLLOWING DEFICIENCIES
YES | Monthly Fire Alarm System Testing done?
Quantity | Description |  |  |  | Location | Owner Responsible Blurbs
| Elevator shaft & pit devices were not accessible during this year’s annual inspection. Please ensure an elevator contractor is booked during our inspection next year to access & test these devices. We had no access to the heat detector in East Storage by 613 from 2023 - 2025. Please arrange for access at next annual inspection. |  |  |  |  | Scenario | Blurb
[6 empty] | Pac Pro Blurb | Your current Fire Alarm System is no longer supported by the manufacturer and the existing field wiring throughout your building is not compatible with today’s Conventional and Addressable Fire Alarm Systems. Under the due diligence category, we strongly suggest owners and/or management budget for the eventual upgrade of the fire alarm system. Please contact us for more information and inquire about upgrading your building's Fire Alarm System.
[6 empty] | Recalled Heat Detectors | Please be advised that the Edwards 281C heat detector has been recalled. We have found “X” devices in your building and marked them on the logbook. They have passed testing. Please let us know if you would like a quote for their replacement.
DEFICIENCIES | [5 empty] | Fire Doors Not Latching | Fire Doors require service. Doors release from magnet as intended. However, doors do not latch closed to maintain fire separation. Site to have repaired.
Fire Alarm System | [5 empty] | FA Programming Required | (Devices) are (describe issue). These devices have been marked on the log report. We recommend engaging with the manufacturers representative. If you would like this issue to be resolved, please reach out to Cantec directly.
Quantity | Description |  |  |  |  | FA device obstructed | (device) is (blocked/obstructed/hidden). Please advise tenant/owner to clear space around the (device) to ensure it is clearly visible and accessible.
1 | Active trouble on Fire Alarm Control Panel - 6th Floor West Hall by Elevator (LCL TROUBLE P01 C02 D 077). Further investigation required. Cantec to engage Troy Life and Safety. |  |  |  |  | FA device removed | (device) has been removed from the fire alarm system. Any modification to the fire alarm system must be documented & verified. Site to provide verification documentation.
[6 empty] | Smoke alarm missing | Smoke alarm has been removed. Tenant is responsible for this device. Site to ensure device is re-installed.
[6 empty] | Smoke alarm removed due to renovations | Several smoke alarm devices on (Location) have been removed due to ongoing construction. Site to ensure these devices will be remounted as per code once construction has been completed.
Emergency Lighting Units
Quantity | Description |  |  |  |  | Fire Alarm Blurbs
11 | Emergency light batteries failed. Replacements required. |  |  |  |  | Scenario | Blurb
[6 empty] | Painted Horn | Horn requires replacement. Device works, but has been painted over.
[6 empty] | Painted Bell | Bell requires replacement. Device works, but has been painted over.
Portable Fire Extinguishers | [5 empty] | Painted Heat Detector | Heat detector has been painted over. Replacement required.
Quantity | Description |  |  |  |  | FACP Bulb Burnt out | "X" bulb on "location" is burnt out. Replacement required.
Occupant Use Hoses
Quantity | Description
Other | [5 empty] | Other Blurbs
Quantity | Description |  |  |  |  | Scenario | Blurb
70 | Smoke alarms have reached the point in time where manufacturers and fire departments recommend replacement. |  |  |  |  | SA due (singular) | Smoke alarm has reached the point in time when both manufacturers and fire departments recommend replacement.
1 | Smoke alarm failed. Replacement required. |  |  |  |  | SA's due (multiple) | Smoke alarms have reached the point in time when both manufacturers and fire departments recommend replacements.
@Kane? we don't need this c.1 appendix section D blurb anymore- correct? Correct - Removed

## EXT only
ANNUAL FIRE EXTINGUISHER INSPECTION LOG
NOTE: Fire Extinguishers are to be maintained in accordance with NFPA #10
| Date: | May 21 - 23, 2025 |  |  | Address: | 655 Douglas Street
ACTIVITY LEGEND | [5 empty] | RP | Repaired
✔ | Tested | TO | Tested by Others | ND | No Device | R | Replaced | Extinguisher is outside of NFPA standards. Replace next service date with new.
✖ | Failed | NA | No Access | NT | Not Tested | RB | Replaced Battery
ACT | LOCATION |  | UNIT TYPE | LAST SERVICE | NEXT SERVICE | NOTE LEGEND
✔ | Elevator Mechanical Room |  | 10LB ABC | 2020 | 2026 |  |  |  | ✔
✖
| 8TH FLOOR | [7 empty] | TO
✔ | East by 810 |  | 5LB ABC | 2022 | 2028 |  |  |  | NA
✔ | West by 802 |  | 5LB ABC | 2022 | 2028 |  |  |  | ND
NT
RP
| 7TH FLOOR | [7 empty] | R
✔ | East by 712 |  | 5LB ABC | 2022 | 2028 |  |  |  | RB
R | Center by 718 |  | 5LB ABC | 2025 | 2031
✔ | West by 702 |  | 5LB ABC | 2020 | 2026
6TH FLOOR
✔ | West by 602 |  | 5LB ABC | 2020 | 2026
✔ | Center by 618 |  | 5LB ABC | 2023 | 2029
✔ | East by 612 |  | 5LB ABC | 2022 | 2028
5TH FLOOR
✔ | East by 512 |  | 5LB ABC | 2022 | 2028
✔ | East by 513 |  | 5LB ABC | 2020 | 2026
✔ | Centre by 518 |  | 5LB ABC | 2022 | 2028
4TH FLOOR
✔ | West by 402 |  | 5LB ABC | 2020 | 2026
✔ | Center by 418 |  | 5LB ABC | 2022 | 2028
✔ | East by 412 |  | 5LB ABC | 2022 | 2028
3RD FLOOR
✔ | East by 312 |  | 5LB ABC | 2023 | 2029
✔ | Center by 318 |  | 5LB ABC | 2024 | 2030
✔ | West by 302 |  | 5LB ABC | 2020 | 2026
2ND FLOOR
✔ | West by 202 |  | 5LB ABC | 2020 | 2026
✔ | Center by 218 |  | 5LB ABC | 2024 | 2030
✔ | West by 212 |  | 5LB ABC | 2022 | 2028
1ST FLOOR
✔ | East Exit |  | 5LB ABC | 2021 | 2027
✔ | West Lobby |  | 5LB ABC | 2020 | 2026
✔ | Lounge |  | 5LB ABC | 2020 | 2026
✔ | Office |  | 5LB ABC | 2020 | 2026
continued on next page
BASEMENT
✔ | Workshop |  | 10LB ABC | 2020 | 2026
✔ | Workshop (Spare) |  | 5LB ABC | 2022 | 2026
✔ | Gym |  | 5LB ABC | 2020 | 2026
✔ | Generator Room |  | 5LB ABC | 2023 | 2029
✔ | Boiler Room East |  | 10LB ABC | 2020 | 2026
✔ | Boiler Room West |  | 10LB ABC | 2024 | 2030
✔ | Electrical Room |  | 5LB ABC | 2022 | 2028
✔ | East Stairs Parkade Access |  | 5LB ABC | 2022 | 2026
East Locker Room (Utility Room 4)
✔ | Locker Room 1 |  | 10LB ABC | 2023 | 2029
Glass Cabinet Dimensions:
EXTs on Full Report - Automated Processor

## ELU only
ANNUAL EMERGENCY LIGHTING UNIT LOG
NOTE: Emergency Lighting Units shall be maintained in accordance with the 2024 BC Fire Code
NOTE 2: Canadian Electrical codes are referenced within BC Fire Code CSA C22.1:24 & CSA C282-15
| Date: | May 21 - 23, 2025 |  |  | Address: | 655 Douglas Street
ACTIVITY LEGEND | [5 empty] | RP | Repaired
✔ | Tested | TO | Tested by Others | ND | No Device | R | Replaced
✖ | Failed | NA | No Access | NT | Not Tested | RB | Replaced Battery
ACT | LOCATION |  | UNIT TYPE | BATTERY TYPE | LAST NEW BATTERY | NOTE LEGEND
✔ | Elevator Mechanical Room Access |  | 24V 360W | 12V 34AH X2 |  | Panel 7B, Breaker 34 |  | ✔
✖
✔ | Stair 1 Exit by 802 |  | RM EXIT |  |  | Button Test |  | TO
✔ | Exit by 801 |  | RM EXIT |  |  | Button Test |  | NA
ND
✔ | By 805 |  | RM EXIT |  |  | Button Test (test button on top of unit) |  | NT
✔ | By 806 |  | RM EXIT |  |  | Panel 7B, Breaker 38 |  | RP
✔ | By 808 |  | RM EXIT |  |  | Panel 7B, Breaker 38 |  | R
✔ | By 811 |  | RM EXIT |  |  | Panel 7B, Breaker 38 |  | RB
✔ | Utility Room by 811 |  | RG24S550VA | 12V 34AH X2 |  | Panel 7B, Breaker 42
✔ | By 809 |  | RM EXIT |  |  | Panel 7B, Breaker 38
✔ | Stair 2 Exit by 810 |  | RM EXIT |  |  | Panel 7B, Breaker 38
7TH FLOOR
✔ | Stair 1 Exit by 704 |  | RM EXIT |  |  | Button Test
✔ | By 702 |  | RM EXIT
✔ | By 702 |  | 6V 36W | 6V 12AH |  | Button Test
F | By 718 |  | 6V 36W | 6V 12AH |  | Button Test
✔ | By 717 |  | RM EXIT |  |  | Button Test
✔ | By 707 |  | RM EXIT |  |  | Panel V, Breaker 26
✔ | Outside 708 |  | 6V 36W |  |  | Button Test
✔ | By 713 |  | RM EXIT |  |  | Panel V, Breaker 26
✔ | Elecrical Room by 713 |  | RG24S550VA | 12V 34AH X2 |  | Panel V, Breaker 28
✔ | By 711 |  | RM EXIT |  |  | Panel V, Breaker 26
✔ | Stair 2 Exit by 712 |  | RM EXIT |  |  | Panel V, Breaker 26
6TH FLOOR
✔ | Stair 1 Exit by 604 |  | RM EXIT |  |  | Button Test
✔ | By 602 |  | RM EXIT |  |  | Button Test
✔ | By 602 |  | 6V 36W | 6V 12AH | 2023 | Button Test
✔ | By 618 |  | 6V 36W | 6V 12AH |  | Button Test
✔ | By 617 |  | RM EXIT |  |  | Button Test
✔ | By 607 |  | RM EXIT |  |  | Button Test
✔ | By 608 |  | 6V 36W | 6V 12AH |  | Button Test
✔ | By 613 |  | RM EXIT |  |  | Panel U, Breaker 22
✔ | Elecrical Room by 613 |  | RG24S550VA | 12V 34AH X2 |  | Panel U, Breaker 24
✔ | Exit by 611 |  | RM EXIT |  |  | Panel U, Breaker 22
✔ | By 612 |  | RM EXIT |  |  | Panel U, Breaker 22
continued on next page
5TH FLOOR
✔ | Stair 1 Exit by 504 |  | RM EXIT |  |  | Button Test
✔ | By 502 |  | RM EXIT |  |  | Button Test
✔ | By 502 |  | 6V 36W | 6V 12AH |  | Breaker 6 (Closet by 202)
F | By 518 |  | 6V 36W | 6V 12AH |  | Breaker 6 (Closet by 202)
✔ | By 517 |  | RM EXIT |  |  | Button Test
✔ | By 507 |  | RM EXIT |  |  | Button Test
✔ | By 508 |  | 6V 36W | 6V 12AH |  | Breaker 6 (Closet by 202)
✔ | By 513 |  | RM EXIT |  |  | Panel R, Breaker 26
F | Electrical Room by 513 |  | RG24S550VA | 12V 34AH X2 |  | Panel R, Breaker 28
✔ | By 511 |  | RM EXIT |  |  | Panel R, Breaker 26
✔ | Stair 2 Exit by 512 |  | RM EXIT |  |  | Panel R, Breaker 26
4TH FLOOR
NT | Stairwell West, Unit A |  | RG24S550VA | 12V 34AH X2 | 2023 | 1st, 7th & 8th Floor Stairwell Not Tested May 2025 due to time restraints
NT | Stairwell West, Unit B |  | RG24S550VA | 12V 34AH X2 |  | 2nd - 6th Floor Stairwell Not Tested May 2025 due to time restraints
✔ | Stair 1 Exit by 404 |  | RM EXIT |  |  | Button Test
✔ | Exit by 402 |  | RM EXIT |  |  | Button Test
✔ | Outside 402 |  | 6V 36W | 6V 12AH |  | Breaker 4 (Closet by 202)
✔ | Outside 418 |  | 6V 36W | 6V 12AH |  | Breaker 4 (Closet by 202)
✔ | Fire Door Exit by 417 |  | RM EXIT |  |  | Button Test
✔ | Fire Door Exit by 407 |  | RM EXIT |  |  | Button Test
F | Outside 408 |  | 6V 36W | 6V 12AH |  | Breaker 4 (Closet by 202)
✔ | Exit by 413 |  | RM EXIT |  |  | Panel T, Breaker 24
✔ | Electrical Room by 413 |  | RG24S550VA | 12V 34AH X2 |  | Panel T, Breaker 26
✔ | Stair 2 Exit by 413 |  | RM EXIT |  |  | Panel T, Breaker 24
✔ | Exit by 411 |  | RM EXIT |  |  | Panel T, Breaker 24
NT | Stairwell East, Unit A |  | RG24S550VA | 12V 34AH X2 | 2023 | 4th Floor Stairwell and up Not Tested May 2025 due to time restraints.
NT | Stairwell East, Unit B |  | RG24S550VA | 12V 34AH X2 |  | 3rd Floor Stairwell and down Not Tested May 2025 due to time restraints.
continued on next page
3RD FLOOR
✔ | Stair 1 Exit by 304 |  | RM EXIT |  |  | Button Test
✔ | Exit by 302 |  | RM EXIT |  |  | Button Test
✔ | Outside 302 |  | 6V 36W | 6V 12AH |  | Breaker 2 (Closet by 202)
✔ | Outside 318 |  | 6V 36W | 6V 12AH |  | Breaker 2 (Closet by 202)
✔ | Fire Door Exit by 317 |  | RM EXIT |  |  | Button Test
✔ | Fire Doors Exit by 307 |  | RM EXIT |  |  | Button Test
F | Outside 308 |  | 6V 36W | 6V 12AH |  | Breaker 2 (Closet by 202)
✔ | Exit by 313 |  | RM EXIT |  |  | Panel Q, Breaker 26
✔ | Electrical Room by 313 |  | RG24S550VA | 12V 34AH X2 | 2023 | Panel Q, Breaker 28
✔ | Stair 2 Exit by 313 |  | RM EXIT |  |  | Panel Q, Breaker 26
✔ | Exit by 311 |  | RM EXIT | NICAD 2W X2 | 2023 | Panel Q, Breaker 26
2ND FLOOR
✔ | Stair 1 by Exit 204 |  | RM EXIT |  |  | Breaker 1 (Utility Room by 202)
✔ | Exit 202 |  | RM EXIT |  |  | Breaker 1 (Utility Room by 202)
F | Outside 202 |  | 6V 36W | 6V 12AH |  | Breaker 3 (Utility Room by 202)
✔ | Outside 218 |  | 6V 36W | 6V 12AH |  | Breaker 3 (Utility Room by 202)
✔ | Fire Door Exit by 217 |  | RM EXIT |  |  | Breaker 1 (Utility Room by 202)
✔ | Fire Door Exit by 207 |  | RM EXIT |  |  | Breaker 1 (Utility Room by 202)
✔ | Outside 208 |  | 6V 36W | 6V 12AH | 2023 | Breaker 3 (Utility Room by 202)
✔ | Exit by 213 |  | RM EXIT |  |  | Panel S, Breaker 26
✔ | Electrical Room by 213 |  | RG24S550VA | 12V 34AH X2 |  | Panel S, Breaker 28
✔ | Exit by 211 |  | RM EXIT |  |  | Panel S, Breaker 26
✔ | Stair 2 Exit by 212 |  | RM EXIT |  |  | Panel S, Breaker 26
665 DOUGLAS STREET - PRESENTATION CENTRE
TO | Lobby Exit |  | RM EXIT |  |  | Electrical Room Panel P Breaker 2
TO | Reception |  | RM EXIT |  |  | Electrical Room Panel P Breaker 2
TO | Office Hall | E | RM EXIT |  |  | Electrical Room Panel P Breaker 2
TO | Office Hall | W | RM EXIT |  |  | Electrical Room Panel P Breaker 2
TO | Exit to Parking | NE | RM EXIT |  |  | Electrical Room Panel P Breaker 2
TO | Office | NW | RM EXIT |  |  | Electrical Room Panel P Breaker 2
TO | Reception |  | CM-PB-E |  |  | Electrical Room Panel P Breaker 4
TO | Office Hall | C | CM-PB-E |  |  | Electrical Room Panel P Breaker 4
TO | Washroom |  | CM-PB-E |  |  | Electrical Room Panel P Breaker 8
TO | Office Hall | E | CM-PB-E |  |  | Electrical Room Panel P Breaker 4
TO | Washroom by Exit to Parking |  | CM-PB-E |  |  | Electrical Room Panel P Breaker 8
continued on next page
TO | Electrical Room |  | CM-PB-E |  |  | Electrical Room Panel P Breaker 8
TO | Office | W | CM-PB-E |  |  | Electrical Room Panel P Breaker 4
TO | Office | NW | CM-PB-E |  |  | Electrical Room Panel P Breaker 4
TO | Lunch Room |  | CM-PB-E |  |  | Electrical Room Panel P Breaker 4
TO | Lab | N | CM-PB-E |  |  | Electrical Room Panel P Breaker 10
TO | Lab | S | CM-PB-E |  |  | Electrical Room Panel P Breaker 10
MAIN FLOOR
✔ | Lobby Exit |  | RM EXIT |  |  | Main Electrical Room Panel A Breaker 20A
✔ | Lounge Exit |  | RM EXIT |  |  | Main Electrical Room Panel A Breaker 20A
✔ | By Rental Office | E | RM EXIT |  |  | Main Electrical Room Panel A Breaker 20A
✔ | By Rental Office | W | RM EXIT |  |  | Main Electrical Room Panel A Breaker 20A
✔ | By Rental Office / Elevator Lobby |  | RM EXIT |  |  | Main Electrical Room Panel A Breaker 20A
✔ | Exit Hall to Parking |  | RM EXIT |  |  | Main Electrical Room Panel A Breaker 20A
F | Office |  | RG24S550VA | 12V 34AH X2 |  | Main Electrical Room Panel A Breaker 29B
BASEMENT
✔ | Basement Hall by Fitness |  | RM EXIT |  |  | Main Electrical Room Panel A Breaker 33B
✔ | Exit to Parking Stair 1 |  | RM EXIT |  |  | Main Electrical Room Panel A Breaker 33B
✔ | Exit outside Maintenance Shop |  | RM EXIT |  |  | Main Electrical Room Panel A Breaker 33B
✔ | Fitness Room |  | RM EXIT |  |  | Main Electrical Room Panel A Breaker 33B
F | Communication Room in Maintenance Shop |  | RG24S550VA | 12V 34AH X2 |  | Main Electrical Room Panel B Breaker 34
✔ | Boiler Room Exit |  | RM EXIT |  |  | Main Electrical Room Panel A Breaker 10A
✔ | Generator Room |  | 6v160w | 6V 12AH |  | Button Test
✔ | Parking Bike Room |  | RG24S550VA | 12V 34AH X2 |  | Main Electrical Room Panel B Breaker 36
✔ | Parking Bike Room | E | RM EXIT |  |  | Main Electrical Room Panel B Breaker 28A
✔ | Parking Bike Room | C | RM EXIT |  |  | Main Electrical Room Panel B Breaker 28A
✔ | Parking Bike Room | S | RM EXIT |  |  | Main Electrical Room Panel B Breaker 28A
✔ | Parking Bike Room | SW | RM EXIT |  |  | Main Electrical Room Panel B Breaker 28A
✔ | Exit Corridor Parkade | W | RM EXIT |  |  | Main Electrical Room Panel B Breaker 28A
ELUs on Full Report - Automated Processor

## HOSES only
ANNUAL OCCUPANT USE HOSE LOG
NOTE: Occupant Use Hoses shall be maintained in accordance with the 2024 BC Fire Code
NOTE: Occupant Use Hoses shall be maintained in accordance with NFPA #1962
| Date: | May 21 - 23, 2025 |  |  | Address: | 655 Douglas Street
ACTIVITY LEGEND | [5 empty] | RP | Repaired
✔ | Tested | TO | Tested by Others | ND | No Device | R | Replaced
✖ | Failed | NA | No Access | NT | Not Tested | RB | Replaced Battery
ACT | LOCATION |  | LENGTH | DATE INSTALLED | LAST SERVICE | NEXT SERVICE | NOTE
✔
✖
TO
NA
ND
NT
RP
R
RB

## 20.1 ¦ Report
ANNUAL FIRE ALARM SYSTEM TEST AND INSPECTION RECORD
20.1 Fire Alarm System Annual Test and Inspection Report
| Inspection Date (DD/MMM/YYYY): |  |  |  | May 21 - 23, 2025
Report Revision Date (DD/MMM/YYYY):
| Building Name: |  |  |  | The Q Apartments | [11 empty] | Craig Shepherd | Kane Wyatt
|  |  |  | Address: | 655 Douglas Street
|  |  |  | City, Province, Postal Code: | [12 empty] | Adam Bendorffe | Denver Fatt
|  |  |  | Building owner or representative's name: | Concert Realty Services Ltd.
| System manufacturer: |  | Edwards | [13 empty] | Jon Graves | Eric Turko
| Model number: |  | QuickStart
| System provides: |  | TRUE | Single Stage Operation |  | FALSE | Two Stage Operation | [9 empty] | James Martyn | Crosby Stewart
| FALSE | Other (describe special operation):
| The fire alarm system is connected to a fire signal receiving centre | [7 empty] | Yes |  | FALSE |  | No |  | FALSE | FALSE | Alex Turko | Jordan Zwicker
| name, if applicable: | [14 empty] | FALSE
| This Report comprises of |  | ? | pages | [12 empty] | Colin Peterson | Kyler Dickey
| The entire fire alarm system has been inspected and tested in accordance with CAN/ULC-S536:2019, Inspection and Testing of Fire Alarm Systems | [7 empty] | Yes |  | TRUE |  | No |  | FALSE |  | Justin Walker | James McNeil
| The fire alarm system is fully functional. | [7 empty] | Yes |  | TRUE |  | No |  | FALSE
| During the Annual Inspection and Test were any Deficiencies Identified? See Page 2, if applicable. | [7 empty] | Yes |  | TRUE |  | No |  | FALSE |  | Austin Rasmussen | William Daniel
As of the following Date (M/D/Y) all identified Deficiencies have been corrected:
| During the Annual Inspection and Test were any Recommendations Identified? See Page 3, if applicable. | [7 empty] | Yes |  | FALSE |  | No |  | FALSE |  | Seth Ealing | Jon Palahicky
The following person is responsible for ensuring that the information contained in this Test and Inspection Report is correct and complete:
Printed Name: | [7 empty] | C. Stewart | [8 empty] | Mariah Grier | Hannah Feness
Certificate/ID Number (short formed)
|  |  |  | Signature (This certifies that the information contained in this Fire Alarm System Annual Test and Inspection Report is correct and complete) | [12 empty] | Kevin Gao | Lilah Weston
| Company Conducting Test: | [6 empty] | Cantec Fire Alarms Ltd.
| Company Phone Number: | [6 empty] | 1 (250) 475-6077
| Was there a secondary person who conducted the Test and Inspection? | [6 empty] | Yes |  | FALSE |  | No |  | FALSE
Printed Name: | [7 empty] | J. Palahicky
Certificate/ID Number (short formed)
Signature (This certifies that the information contained in this Fire Alarm System Annual Test and Inspection Report is correct and complete)
| Company Conducting Test: | [6 empty] | Cantec Fire Alarms Ltd.
| Company Phone Number: | [6 empty] | 1 (250) 475-6077
Note on F7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Linked to cover page, 33.2 device, 33.5 signalling
Note on F9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Linked to cover page, 33.2 device, 33.5 signalling
Note on F10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Linked to cover page, 33.2 device, 33.5 signalling
Note on F12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Linked to cover page

## 20.2 ¦ Deficiencies
20.2 Deficiencies
NOTE: System and device installation locations may differ from those described in CAN/ULC-S524 if a performance based design and alternate solution documents were submitted and approved by the authority having jurisdiction for the system under test.
The Inspection and Testing of any corrections/repairs of deficiencies noted on this form has been completed by qualified personnel in the column marked "Technician Name & Certificate No.”
Item # | Device type | Device location | Deficiency | CAN/ULC-S536 Standard reference clause | Date corrected (M/D/Y) | Work order or reference no. | Company which corrected deficiency | Technician name & certificate no.
1
2
3
4
5
6
7
8
9
10
I understand that all Deficiencies noted in the table above have been corrected:
Building Owner / Owner's Representative Name:
Building Owner / Owner's Representative Signature:
Date of Signature:
NOTE 1: Only the above table needs to be updated on correction of deficiencies. The entire report does not have to be reissued.
NOTE 2: Please see the main Deficiency Summary page for site wide summary of all serviceable life and fire safety equipment
NOTE 3: Cantec completes Annunciator testing procedures at the primary FD response only. A lamp test and confirmation of AC power will be completed at all other remote annunciator panels. Fire Alarm Panel and Annunciator device identification may be confirmed on alternate years.
NOTE 4: Unless otherwise provided at the FACP or within a building's Fire Safety Plan, Cantec is unable to confirm as-designed Sequence of Events.
NOTE 5: Manometer testing to confirm positive airflow and/or pressure differential in air duct type smoke detectors may not have been confirmed per manufacture's specifications. Device has been inspected and tested to confirm operability.
NOTE 6: Smoke Detector Sensitivity may be tested during the inspection if time permits.
NOTE 7: Isolators and End-of-Line Resistors may not have been tested for open circuit, ground fault and short conditions unless time permits. This includes 23.3 Circuit Fault Tolerance Testing. See Log Report for details.

## 20.3 ¦ Recommendations
20.3 Recommendations
Recommendations - page 3
20.4 Technician Attendance Log
NOTE: See 7.4
Date (MM/DD/YY) | Time in / Time out | Notes (for the day) | Primary technician printed name |  | Primary technician certification no.
Note
Recommendations |  |  |  | Deficiencies
20.3.1: For the purpose of this standard, Recommendation is a proposal or suggestion as to the best course of action for improvement of system components or system operation / installations, including safety considerations, such as: |  |  |  | 20.2.1: For the purpose of this Standard, deficiency refers to a device or function that: a) Does not operate as intended b) Due to alteration in the building layout or contents, is installed in a location which is not readily accessible for service, testing, maintenance purposes due to safety considerations, and was not tested in the last 24 months; c) Is installed in an environment which is not compatible with the documented operating conditions of the specific device; or d) is installed in an orientation or location not specifically indicated by the installation instruction of the specific device.
a) Identifying antiquated or obsolete equipment; b) Availability of newer cost effective technology; or c) Alternate methods of detection.

## 21 ¦ Documentation
21 Documentation
NOTE: See Section 7. Documentation
21.1 Documentation for the fire alarm system is available or accessible on site and includes the following description of the fire alarm system:
A | Instructions for resetting the system and silencing alarm signals. | Yes |  | FALSE | No |  | FALSE
B | Instructions for silencing the trouble signal and action to be taken when the trouble signal sounds. | Yes |  | FALSE | No |  | FALSE
C | Description of the function of each operating control and indicator on the fire alarm unit. | Yes |  | FALSE | No |  | FALSE
D | Description of the area or fire zone protected by each alarm detection circuit (this may be in the form of a list or plan drawing). | Yes |  | FALSE | No |  | FALSE
E | Description of alarm signal operation. | Yes |  | FALSE | No |  | FALSE
F | Description of ancillary equipment controlled by the fire alarm system. | Yes |  | FALSE | No |  | FALSE
G | In systems that provide logical control of a smoke control system, documentation is on site and includes a sequence of operation of the smoke control system. | Yes | FALSE | No | FALSE | N/A | FALSE
H | Building diagrams are on site that clearly indicate the type and location of all smoke-control equipment (fans, dampers, etc.). | Yes | FALSE | No | FALSE | N/A | FALSE
I | Description of the fire alarm system: i) Sequence of operation (see Annex D) | Yes |  | FALSE | No |  | FALSE
| ii) Operating instruction (see Annex D) | Yes |  | FALSE | No |  | FALSE
| iii) Description of each type of field device | Yes |  | FALSE | No |  | FALSE
| iv) Details of input to programmed output functions for programmed systems | Yes |  | FALSE | No |  | FALSE
| v) Connection to a fire signal receiving centre, if required by applicable codes and regulations | Yes |  | FALSE | No |  | FALSE
| vi) Previous verification report(s) and all documentation related to any modification showing approval of such modifications by the AHJ, if applicable | Yes | FALSE | No | FALSE | N/A | FALSE
| vii) The as-built drawings of the building fire alarm system (See Annex D) | Yes |  | FALSE | No |  | FALSE
| viii) Copy of the site specific software (if applicable) | Yes | FALSE | No | FALSE | N/A | FALSE
J | Indicate location(s)and media type(s) of documentation:

## 22.1 ¦ CU or Transp Insp
22 Control Unit or Transponder Inspection
| YES | FALSE | = Operated Correctly | NO | FALSE | = Did not operate correctly | N/A | FALSE | = Not applicable
|  |  |  | (Refer to Deficiencies, 20.2) |  |  | Function or feature not provided on this fire alarm system
22.1 Control Unit or Transponder Inspection
NOTE 1 : See Clause 8.2 in CAN/ULC-S536-19
NOTE 2: Complete section for each control unit or transponder.
Control unit or transponder location: |  |  |  | Parkade Electrical Room
Control unit or transponder identification: |  |  |  | Edwards QuickStart
A |  | Input circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
B |  | Output circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
C |  | Correct designations for common control functions and indicators. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
D |  | Plug-in components and modules securely in place. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
E |  | Plug-in cables securely in place. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
F |  | (i) Record the date, revision and version of firmware. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
|  | (ii) Record the date, revision and version of software program. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
G |  | Control unit and transponder are clean and free of dust and dirt. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
H |  | Fuses in accordance with manufacturer's specification. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
I |  | Control unit or transponder lock functional. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
J |  | Termination points from wiring to field devices secure. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
22 Control Unit or Transponder Inspection
| YES | FALSE | = Operated Correctly | NO | FALSE | = Did not operate correctly | N/A | FALSE | = Not applicable
|  |  |  | (Refer to Deficiencies, 20.2) |  |  | Function or feature not provided on this fire alarm system
22.1 Control Unit or Transponder Inspection
NOTE 1 : See Clause 8.2 in CAN/ULC-S536-19
NOTE 2: Complete section for each control unit or transponder.
Control unit or transponder location: |  |  |  | 5th Floor West Closet
Control unit or transponder identification: |  |  |  | Booster Panel
A |  | Input circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | TRUE
B |  | Output circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
C |  | Correct designations for common control functions and indicators. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
D |  | Plug-in components and modules securely in place. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
E |  | Plug-in cables securely in place. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
F |  | (i) Record the date, revision and version of firmware. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
|  | (ii) Record the date, revision and version of software program. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
G |  | Control unit and transponder are clean and free of dust and dirt. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
H |  | Fuses in accordance with manufacturer's specification. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
I |  | Control unit or transponder lock functional. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
J |  | Termination points from wiring to field devices secure. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
22 Control Unit or Transponder Inspection
| YES | FALSE | = Operated Correctly | NO | FALSE | = Did not operate correctly | N/A | FALSE | = Not applicable
|  |  |  | (Refer to Deficiencies, 20.2) |  |  | Function or feature not provided on this fire alarm system
22.1 Control Unit or Transponder Inspection
NOTE 1 : See Clause 8.2 in CAN/ULC-S536-19
NOTE 2: Complete section for each control unit or transponder.
Control unit or transponder location:
Control unit or transponder identification:
A |  | Input circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Output circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Correct designations for common control functions and indicators. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
D |  | Plug-in components and modules securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
E |  | Plug-in cables securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
F |  | (i) Record the date, revision and version of firmware. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
|  | (ii) Record the date, revision and version of software program. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
G |  | Control unit and transponder are clean and free of dust and dirt. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Fuses in accordance with manufacturer's specification. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Control unit or transponder lock functional. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Termination points from wiring to field devices secure. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
22 Control Unit or Transponder Inspection
| YES | FALSE | = Operated Correctly | NO | FALSE | = Did not operate correctly | N/A | FALSE | = Not applicable
|  |  |  | (Refer to Deficiencies, 20.2) |  |  | Function or feature not provided on this fire alarm system
22.1 Control Unit or Transponder Inspection
NOTE 1 : See Clause 8.2 in CAN/ULC-S536-19
NOTE 2: Complete section for each control unit or transponder.
Control unit or transponder location:
Control unit or transponder identification:
A |  | Input circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Output circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Correct designations for common control functions and indicators. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
D |  | Plug-in components and modules securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
E |  | Plug-in cables securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
F |  | (i) Record the date, revision and version of firmware. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
|  | (ii) Record the date, revision and version of software program. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
G |  | Control unit and transponder are clean and free of dust and dirt. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Fuses in accordance with manufacturer's specification. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Control unit or transponder lock functional. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Termination points from wiring to field devices secure. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
22 Control Unit or Transponder Inspection
| YES | FALSE | = Operated Correctly | NO | FALSE | = Did not operate correctly | N/A | FALSE | = Not applicable
|  |  |  | (Refer to Deficiencies, 20.2) |  |  | Function or feature not provided on this fire alarm system
22.1 Control Unit or Transponder Inspection
NOTE 1 : See Clause 8.2 in CAN/ULC-S536-19
NOTE 2: Complete section for each control unit or transponder.
Control unit or transponder location:
Control unit or transponder identification:
A |  | Input circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Output circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Correct designations for common control functions and indicators. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
D |  | Plug-in components and modules securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
E |  | Plug-in cables securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
F |  | (i) Record the date, revision and version of firmware. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
|  | (ii) Record the date, revision and version of software program. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
G |  | Control unit and transponder are clean and free of dust and dirt. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Fuses in accordance with manufacturer's specification. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Control unit or transponder lock functional. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Termination points from wiring to field devices secure. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
22 Control Unit or Transponder Inspection
| YES | FALSE | = Operated Correctly | NO | FALSE | = Did not operate correctly | N/A | FALSE | = Not applicable
|  |  |  | (Refer to Deficiencies, 20.2) |  |  | Function or feature not provided on this fire alarm system
22.1 Control Unit or Transponder Inspection
NOTE 1 : See Clause 8.2 in CAN/ULC-S536-19
NOTE 2: Complete section for each control unit or transponder.
Control unit or transponder location:
Control unit or transponder identification:
A |  | Input circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Output circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Correct designations for common control functions and indicators. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
D |  | Plug-in components and modules securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
E |  | Plug-in cables securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
F |  | (i) Record the date, revision and version of firmware. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
|  | (ii) Record the date, revision and version of software program. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
G |  | Control unit and transponder are clean and free of dust and dirt. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Fuses in accordance with manufacturer's specification. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Control unit or transponder lock functional. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Termination points from wiring to field devices secure. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
22 Control Unit or Transponder Inspection
| YES | FALSE | = Operated Correctly | NO | FALSE | = Did not operate correctly | N/A | FALSE | = Not applicable
|  |  |  | (Refer to Deficiencies, 20.2) |  |  | Function or feature not provided on this fire alarm system
22.1 Control Unit or Transponder Inspection
NOTE 1 : See Clause 8.2 in CAN/ULC-S536-19
NOTE 2: Complete section for each control unit or transponder.
Control unit or transponder location:
Control unit or transponder identification:
A |  | Input circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Output circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Correct designations for common control functions and indicators. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
D |  | Plug-in components and modules securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
E |  | Plug-in cables securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
F |  | (i) Record the date, revision and version of firmware. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
|  | (ii) Record the date, revision and version of software program. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
G |  | Control unit and transponder are clean and free of dust and dirt. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Fuses in accordance with manufacturer's specification. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Control unit or transponder lock functional. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Termination points from wiring to field devices secure. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
22 Control Unit or Transponder Inspection
| YES | FALSE | = Operated Correctly | NO | FALSE | = Did not operate correctly | N/A | FALSE | = Not applicable
|  |  |  | (Refer to Deficiencies, 20.2) |  |  | Function or feature not provided on this fire alarm system
22.1 Control Unit or Transponder Inspection
NOTE 1 : See Clause 8.2 in CAN/ULC-S536-19
NOTE 2: Complete section for each control unit or transponder.
Control unit or transponder location:
Control unit or transponder identification:
A |  | Input circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Output circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Correct designations for common control functions and indicators. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
D |  | Plug-in components and modules securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
E |  | Plug-in cables securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
F |  | (i) Record the date, revision and version of firmware. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
|  | (ii) Record the date, revision and version of software program. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
G |  | Control unit and transponder are clean and free of dust and dirt. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Fuses in accordance with manufacturer's specification. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Control unit or transponder lock functional. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Termination points from wiring to field devices secure. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE

## 22.2 ¦ CU or Transp Test
22.2 Control Unit or Transponder Test
See 8.3 in CAN/ULC-S536-19
Complete section for each control unit or transponder.
Control unit or transponder location: |  | Parkade Electrical Room
Control unit or transponder identification: |  | Edwards QuickStart
A | Power 'ON' visual indicator operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
B | Time and date indication corresponds with local time and date. |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Common visual trouble signal operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
D | Common audible trouble signal operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
E | Trouble signal silence switch operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
F | Main power supply failure trouble signal operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
G | Trouble signal operates during positive and negative ground fault tests. |  | Yes | TRUE | No | FALSE | N/A | FALSE
H | Alert signal operates. |  | Yes | FALSE | No | FALSE | N/A | TRUE
I | Alarm signal operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
J | Automatic transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | TRUE
Time:
K | Manual transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | TRUE
L | Automatic transfer from alert signal to alarm signal cancel (acknowledge) feature operates on two-stage system. |  | Yes | FALSE | No | FALSE | N/A | TRUE
M | Alarm signal silence inhibit function operates. |  | Yes | FALSE | No | FALSE | N/A | TRUE
N | Alarm signal manual silence operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
O | Alarm signal silence visual indication operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
P | Alarm signals when silenced, automatically reinitiate upon subsequent alarm from another NBC required fire alarm zone. |  | Yes | TRUE | No | FALSE | N/A | FALSE
Q | Duration of alarm signal prior to automatic silence. |  | Time: |  | No | FALSE | N/A | TRUE
R | Audible and visual alert signals and alarm signals programmed and operate per design and specification; or documentation as provided in Section 21. |  | Time: |  |  |  | N/A | FALSE
S | Input circuit, alarm and supervisory operation, including audible and visual indicator operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
T | Input circuit supervision fault causes a trouble indication. |  | Yes | TRUE | No | FALSE | N/A | FALSE
U | Output circuit alarm indicators operate. |  | Yes | TRUE | No | FALSE | N/A | FALSE
V | Output circuit supervision fault causes a trouble indication. |  | Yes | TRUE | No | FALSE | N/A | FALSE
W | Visual indicator test (lamp test) operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
X | Coded signal sequences operate not less than the required number of times and the correct alarm signal operates thereafter. |  | Yes | FALSE | No | FALSE | N/A | TRUE
Y | Coded signal sequences are not interrupted by subsequent alarms. |  | Yes | FALSE | No | FALSE | N/A | TRUE
Z | Ancillary device by-pass results in a trouble signal. |  | Yes | TRUE | No | FALSE | N/A | FALSE
AA | Input circuit to output circuit operation, including ancillary device circuits, for correct program operation, as per design and specification, or documentation as detailed in D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | TRUE | No | FALSE | N/A | FALSE
BB | System Reset operates |  | Yes | TRUE | No | FALSE | N/A | FALSE
CC | Main power supply to emergency power supply transfer operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
DD | Smoke detector alarm verification (status change confirmation) verified. [Refer to14.4.3, Smoke Detector Alarm Verification (Status Change Confirmation)]. |  | Yes | FALSE | No | FALSE | N/A | TRUE
22.2 Control Unit or Transponder Test
See 8.3 in CAN/ULC-S536-19
Complete section for each control unit or transponder.
Control unit or transponder location: |  | 5th Floor West Closet
Control unit or transponder identification: |  | Booster Panel
A | Power 'ON' visual indicator operates. |  | Yes | TRUE | No | FALSE
B | Time and date indication corresponds with local time and date. |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Common visual trouble signal operates. |  | Yes | TRUE | No | FALSE
D | Common audible trouble signal operates. |  | Yes | FALSE | No | FALSE |  |  | TRUE
E | Trouble signal silence switch operates. |  | Yes | FALSE | No | FALSE |  |  | TRUE
F | Main power supply failure trouble signal operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
G | Trouble signal operates during positive and negative ground fault tests. |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alert signal operates. |  | Yes | FALSE | No | FALSE | N/A | TRUE
I | Alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | TRUE
J | Automatic transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | TRUE
Time:
K | Manual transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | TRUE
L | Automatic transfer from alert signal to alarm signal cancel (acknowledge) feature operates on two-stage system. |  | Yes | FALSE | No | FALSE | N/A | TRUE
M | Alarm signal silence inhibit function operates. |  | Yes | FALSE | No | FALSE | N/A | TRUE
N | Alarm signal manual silence operates. |  | Yes | FALSE | No | FALSE | N/A | TRUE
O | Alarm signal silence visual indication operates. |  | Yes | FALSE | No | FALSE | N/A | TRUE
P | Alarm signals when silenced, automatically reinitiate upon subsequent alarm from another NBC required fire alarm zone. |  | Yes | FALSE | No | FALSE | N/A | TRUE
Q | Duration of alarm signal prior to automatic silence. |  | Time: |  | No | FALSE | N/A | TRUE
R | Audible and visual alert signals and alarm signals programmed and operate per design and specification; or documentation as provided in Section 21. |  | Time: | TRUE |  |  | N/A | FALSE
S | Input circuit, alarm and supervisory operation, including audible and visual indicator operates. |  | Yes | TRUE | No | FALSE
T | Input circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | TRUE
U | Output circuit alarm indicators operate. |  | Yes | TRUE | No | FALSE | N/A | FALSE
V | Output circuit supervision fault causes a trouble indication. |  | Yes | TRUE | No | FALSE | N/A | FALSE
W | Visual indicator test (lamp test) operates. |  | Yes | FALSE | No | FALSE | N/A | TRUE
X | Coded signal sequences operate not less than the required number of times and the correct alarm signal operates thereafter. |  | Yes | FALSE | No | FALSE | N/A | TRUE
Y | Coded signal sequences are not interrupted by subsequent alarms. |  | Yes | FALSE | No | FALSE | N/A | TRUE
Z | Ancillary device by-pass results in a trouble signal. |  | Yes | FALSE | No | FALSE | N/A | TRUE
AA | Input circuit to output circuit operation, including ancillary device circuits, for correct program operation, as per design and specification, or documentation as detailed in D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | TRUE | No | FALSE | N/A | FALSE
BB | System Reset operates |  | Yes | FALSE | No | FALSE |  |  | TRUE
CC | Main power supply to emergency power supply transfer operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
DD | Smoke detector alarm verification (status change confirmation) verified. [Refer to14.4.3, Smoke Detector Alarm Verification (Status Change Confirmation)]. |  | Yes | FALSE | No | FALSE | N/A | TRUE
22.2 Control Unit or Transponder Test
See 8.3 in CAN/ULC-S536-19
Complete section for each control unit or transponder.
Control unit or transponder location: |  | 0
Control unit or transponder identification: |  | 0
A | Power 'ON' visual indicator operates. |  | Yes | FALSE | No | FALSE
B | Time and date indication corresponds with local time and date. |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Common visual trouble signal operates. |  | Yes | FALSE | No | FALSE
D | Common audible trouble signal operates. |  | Yes | FALSE | No | FALSE
E | Trouble signal silence switch operates. |  | Yes | FALSE | No | FALSE
F | Main power supply failure trouble signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Trouble signal operates during positive and negative ground fault tests. |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alert signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Automatic transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Time:
K | Manual transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Automatic transfer from alert signal to alarm signal cancel (acknowledge) feature operates on two-stage system. |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Alarm signal silence inhibit function operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
N | Alarm signal manual silence operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
O | Alarm signal silence visual indication operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
P | Alarm signals when silenced, automatically reinitiate upon subsequent alarm from another NBC required fire alarm zone. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Q | Duration of alarm signal prior to automatic silence. |  | Time: |  | No | FALSE | N/A | FALSE
R | Audible and visual alert signals and alarm signals programmed and operate per design and specification; or documentation as provided in Section 21. |  | Time: |  |  |  | N/A | FALSE
S | Input circuit, alarm and supervisory operation, including audible and visual indicator operates. |  | Yes | FALSE | No | FALSE
T | Input circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
U | Output circuit alarm indicators operate. |  | Yes | FALSE | No | FALSE | N/A | FALSE
V | Output circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
W | Visual indicator test (lamp test) operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
X | Coded signal sequences operate not less than the required number of times and the correct alarm signal operates thereafter. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Y | Coded signal sequences are not interrupted by subsequent alarms. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Z | Ancillary device by-pass results in a trouble signal. |  | Yes | FALSE | No | FALSE | N/A | FALSE
AA | Input circuit to output circuit operation, including ancillary device circuits, for correct program operation, as per design and specification, or documentation as detailed in D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | FALSE | No | FALSE | N/A | FALSE
BB | System Reset operates |  | Yes | FALSE | No | FALSE
CC | Main power supply to emergency power supply transfer operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
DD | Smoke detector alarm verification (status change confirmation) verified. [Refer to14.4.3, Smoke Detector Alarm Verification (Status Change Confirmation)]. |  | Yes | FALSE | No | FALSE | N/A | FALSE
22.2 Control Unit or Transponder Test
See 8.3 in CAN/ULC-S536-19
Complete section for each control unit or transponder.
Control unit or transponder location: |  | 0
Control unit or transponder identification: |  | 0
A | Power 'ON' visual indicator operates. |  | Yes | FALSE | No | FALSE
B | Time and date indication corresponds with local time and date. |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Common visual trouble signal operates. |  | Yes | FALSE | No | FALSE
D | Common audible trouble signal operates. |  | Yes | FALSE | No | FALSE
E | Trouble signal silence switch operates. |  | Yes | FALSE | No | FALSE
F | Main power supply failure trouble signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Trouble signal operates during positive and negative ground fault tests. |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alert signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Automatic transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Time:
K | Manual transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Automatic transfer from alert signal to alarm signal cancel (acknowledge) feature operates on two-stage system. |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Alarm signal silence inhibit function operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
N | Alarm signal manual silence operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
O | Alarm signal silence visual indication operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
P | Alarm signals when silenced, automatically reinitiate upon subsequent alarm from another NBC required fire alarm zone. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Q | Duration of alarm signal prior to automatic silence. |  | Time: |  | No | FALSE | N/A | FALSE
R | Audible and visual alert signals and alarm signals programmed and operate per design and specification; or documentation as provided in Section 21. |  | Time: |  |  |  | N/A | FALSE
S | Input circuit, alarm and supervisory operation, including audible and visual indicator operates. |  | Yes | FALSE | No | FALSE
T | Input circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
U | Output circuit alarm indicators operate. |  | Yes | FALSE | No | FALSE | N/A | FALSE
V | Output circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
W | Visual indicator test (lamp test) operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
X | Coded signal sequences operate not less than the required number of times and the correct alarm signal operates thereafter. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Y | Coded signal sequences are not interrupted by subsequent alarms. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Z | Ancillary device by-pass results in a trouble signal. |  | Yes | FALSE | No | FALSE | N/A | FALSE
AA | Input circuit to output circuit operation, including ancillary device circuits, for correct program operation, as per design and specification, or documentation as detailed in D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | FALSE | No | FALSE | N/A | FALSE
BB | System Reset operates |  | Yes | FALSE | No | FALSE
CC | Main power supply to emergency power supply transfer operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
DD | Smoke detector alarm verification (status change confirmation) verified. [Refer to14.4.3, Smoke Detector Alarm Verification (Status Change Confirmation)]. |  | Yes | FALSE | No | FALSE | N/A | FALSE
22.2 Control Unit or Transponder Test
See 8.3 in CAN/ULC-S536-19
Complete section for each control unit or transponder.
Control unit or transponder location: |  | 0
Control unit or transponder identification: |  | 0
A | Power 'ON' visual indicator operates. |  | Yes | FALSE | No | FALSE
B | Time and date indication corresponds with local time and date. |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Common visual trouble signal operates. |  | Yes | FALSE | No | FALSE
D | Common audible trouble signal operates. |  | Yes | FALSE | No | FALSE
E | Trouble signal silence switch operates. |  | Yes | FALSE | No | FALSE
F | Main power supply failure trouble signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Trouble signal operates during positive and negative ground fault tests. |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alert signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Automatic transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Time:
K | Manual transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Automatic transfer from alert signal to alarm signal cancel (acknowledge) feature operates on two-stage system. |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Alarm signal silence inhibit function operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
N | Alarm signal manual silence operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
O | Alarm signal silence visual indication operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
P | Alarm signals when silenced, automatically reinitiate upon subsequent alarm from another NBC required fire alarm zone. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Q | Duration of alarm signal prior to automatic silence. |  | Time: |  | No | FALSE | N/A | FALSE
R | Audible and visual alert signals and alarm signals programmed and operate per design and specification; or documentation as provided in Section 21. |  | Time: |  |  |  | N/A | FALSE
S | Input circuit, alarm and supervisory operation, including audible and visual indicator operates. |  | Yes | FALSE | No | FALSE
T | Input circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
U | Output circuit alarm indicators operate. |  | Yes | FALSE | No | FALSE | N/A | FALSE
V | Output circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
W | Visual indicator test (lamp test) operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
X | Coded signal sequences operate not less than the required number of times and the correct alarm signal operates thereafter. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Y | Coded signal sequences are not interrupted by subsequent alarms. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Z | Ancillary device by-pass results in a trouble signal. |  | Yes | FALSE | No | FALSE | N/A | FALSE
AA | Input circuit to output circuit operation, including ancillary device circuits, for correct program operation, as per design and specification, or documentation as detailed in D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | FALSE | No | FALSE | N/A | FALSE
BB | System Reset operates |  | Yes | FALSE | No | FALSE
CC | Main power supply to emergency power supply transfer operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
DD | Smoke detector alarm verification (status change confirmation) verified. [Refer to14.4.3, Smoke Detector Alarm Verification (Status Change Confirmation)]. |  | Yes | FALSE | No | FALSE | N/A | FALSE
22.2 Control Unit or Transponder Test
See 8.3 in CAN/ULC-S536-19
Complete section for each control unit or transponder.
Control unit or transponder location: |  | 0
Control unit or transponder identification: |  | 0
A | Power 'ON' visual indicator operates. |  | Yes | FALSE | No | FALSE
B | Time and date indication corresponds with local time and date. |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Common visual trouble signal operates. |  | Yes | FALSE | No | FALSE
D | Common audible trouble signal operates. |  | Yes | FALSE | No | FALSE
E | Trouble signal silence switch operates. |  | Yes | FALSE | No | FALSE
F | Main power supply failure trouble signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Trouble signal operates during positive and negative ground fault tests. |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alert signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Automatic transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Time:
K | Manual transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Automatic transfer from alert signal to alarm signal cancel (acknowledge) feature operates on two-stage system. |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Alarm signal silence inhibit function operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
N | Alarm signal manual silence operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
O | Alarm signal silence visual indication operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
P | Alarm signals when silenced, automatically reinitiate upon subsequent alarm from another NBC required fire alarm zone. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Q | Duration of alarm signal prior to automatic silence. |  | Time: |  | No | FALSE | N/A | FALSE
R | Audible and visual alert signals and alarm signals programmed and operate per design and specification; or documentation as provided in Section 21. |  | Time: |  |  |  | N/A | FALSE
S | Input circuit, alarm and supervisory operation, including audible and visual indicator operates. |  | Yes | FALSE | No | FALSE
T | Input circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
U | Output circuit alarm indicators operate. |  | Yes | FALSE | No | FALSE | N/A | FALSE
V | Output circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
W | Visual indicator test (lamp test) operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
X | Coded signal sequences operate not less than the required number of times and the correct alarm signal operates thereafter. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Y | Coded signal sequences are not interrupted by subsequent alarms. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Z | Ancillary device by-pass results in a trouble signal. |  | Yes | FALSE | No | FALSE | N/A | FALSE
AA | Input circuit to output circuit operation, including ancillary device circuits, for correct program operation, as per design and specification, or documentation as detailed in D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | FALSE | No | FALSE | N/A | FALSE
BB | System Reset operates |  | Yes | FALSE | No | FALSE
CC | Main power supply to emergency power supply transfer operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
DD | Smoke detector alarm verification (status change confirmation) verified. [Refer to14.4.3, Smoke Detector Alarm Verification (Status Change Confirmation)]. |  | Yes | FALSE | No | FALSE | N/A | FALSE
22.2 Control Unit or Transponder Test
See 8.3 in CAN/ULC-S536-19
Complete section for each control unit or transponder.
Control unit or transponder location: |  | 0
Control unit or transponder identification: |  | 0
A | Power 'ON' visual indicator operates. |  | Yes | FALSE | No | FALSE
B | Time and date indication corresponds with local time and date. |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Common visual trouble signal operates. |  | Yes | FALSE | No | FALSE
D | Common audible trouble signal operates. |  | Yes | FALSE | No | FALSE
E | Trouble signal silence switch operates. |  | Yes | FALSE | No | FALSE
F | Main power supply failure trouble signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Trouble signal operates during positive and negative ground fault tests. |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alert signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Automatic transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Time:
K | Manual transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Automatic transfer from alert signal to alarm signal cancel (acknowledge) feature operates on two-stage system. |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Alarm signal silence inhibit function operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
N | Alarm signal manual silence operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
O | Alarm signal silence visual indication operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
P | Alarm signals when silenced, automatically reinitiate upon subsequent alarm from another NBC required fire alarm zone. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Q | Duration of alarm signal prior to automatic silence. |  | Time: |  | No | FALSE | N/A | FALSE
R | Audible and visual alert signals and alarm signals programmed and operate per design and specification; or documentation as provided in Section 21. |  | Time: |  |  |  | N/A | FALSE
S | Input circuit, alarm and supervisory operation, including audible and visual indicator operates. |  | Yes | FALSE | No | FALSE
T | Input circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
U | Output circuit alarm indicators operate. |  | Yes | FALSE | No | FALSE | N/A | FALSE
V | Output circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
W | Visual indicator test (lamp test) operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
X | Coded signal sequences operate not less than the required number of times and the correct alarm signal operates thereafter. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Y | Coded signal sequences are not interrupted by subsequent alarms. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Z | Ancillary device by-pass results in a trouble signal. |  | Yes | FALSE | No | FALSE | N/A | FALSE
AA | Input circuit to output circuit operation, including ancillary device circuits, for correct program operation, as per design and specification, or documentation as detailed in D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | FALSE | No | FALSE | N/A | FALSE
BB | System Reset operates |  | Yes | FALSE | No | FALSE
CC | Main power supply to emergency power supply transfer operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
DD | Smoke detector alarm verification (status change confirmation) verified. [Refer to14.4.3, Smoke Detector Alarm Verification (Status Change Confirmation)]. |  | Yes | FALSE | No | FALSE | N/A | FALSE
22.2 Control Unit or Transponder Test
See 8.3 in CAN/ULC-S536-19
Complete section for each control unit or transponder.
Control unit or transponder location: |  | 0
Control unit or transponder identification: |  | 0
A | Power 'ON' visual indicator operates. |  | Yes | FALSE | No | FALSE
B | Time and date indication corresponds with local time and date. |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Common visual trouble signal operates. |  | Yes | FALSE | No | FALSE
D | Common audible trouble signal operates. |  | Yes | FALSE | No | FALSE
E | Trouble signal silence switch operates. |  | Yes | FALSE | No | FALSE
F | Main power supply failure trouble signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Trouble signal operates during positive and negative ground fault tests. |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alert signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Automatic transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Time:
K | Manual transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Automatic transfer from alert signal to alarm signal cancel (acknowledge) feature operates on two-stage system. |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Alarm signal silence inhibit function operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
N | Alarm signal manual silence operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
O | Alarm signal silence visual indication operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
P | Alarm signals when silenced, automatically reinitiate upon subsequent alarm from another NBC required fire alarm zone. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Q | Duration of alarm signal prior to automatic silence. |  | Time: |  | No | FALSE | N/A | FALSE
R | Audible and visual alert signals and alarm signals programmed and operate per design and specification; or documentation as provided in Section 21. |  | Time: |  |  |  | N/A | FALSE
S | Input circuit, alarm and supervisory operation, including audible and visual indicator operates. |  | Yes | FALSE | No | FALSE
T | Input circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
U | Output circuit alarm indicators operate. |  | Yes | FALSE | No | FALSE | N/A | FALSE
V | Output circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
W | Visual indicator test (lamp test) operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
X | Coded signal sequences operate not less than the required number of times and the correct alarm signal operates thereafter. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Y | Coded signal sequences are not interrupted by subsequent alarms. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Z | Ancillary device by-pass results in a trouble signal. |  | Yes | FALSE | No | FALSE | N/A | FALSE
AA | Input circuit to output circuit operation, including ancillary device circuits, for correct program operation, as per design and specification, or documentation as detailed in D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | FALSE | No | FALSE | N/A | FALSE
BB | System Reset operates |  | Yes | FALSE | No | FALSE
CC | Main power supply to emergency power supply transfer operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
DD | Smoke detector alarm verification (status change confirmation) verified. [Refer to14.4.3, Smoke Detector Alarm Verification (Status Change Confirmation)]. |  | Yes | FALSE | No | FALSE | N/A | FALSE

## 22.3 + 22.4 ¦ Voice & PS
22.3 Voice Communication Test
NOTE: See Subsection 8.5 in CAN/ULC-S536-19
|  | There are no Voice Communication Capabilities on this system |  | TRUE
A | Power 'ON' visual indicator operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Common visual trouble signal operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Common audible trouble signal operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | Trouble signal silence switch operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | All-call voice paging, including visual indicator, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Output circuits for selective voice paging, including visual indication, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Output circuits for selective voice paging trouble operation, including visual indication, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Microphone, including press to talk switch, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Operation of voice paging does not interfere with initial inhibit time of alert signal or alarm signal. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | All-call voice paging operates (on emergency power supply) |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
K | Where systems use back-up amplifiers, the automatic transfer feature operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Circuits for emergency telephone call-in operation, including audible and visual indication, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Circuits for emergency telephones for operation, including two-way voice communication, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
N | Circuits for emergency telephone trouble operation, including visual indication, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
O | Emergency telephone verbal communication operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
P | Emergency telephone operable or in-use tone at handset operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
Q | In standby mode, a short, or open on a paging, alert, alarm, or emergency telephone voice communication buss results in a buss specific trouble condition. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
22.4 Power Supply Inspection
NOTE: See Subsection 8.5 in CAN/ULC-S536-19
Control unit or transponder location: |  |  | Parkade Electrical Room
Control unit or transponder identification: |  |  | Edwards QuickStart
Circuit disconnect means or breaker location:
Circuit disconnect means or breaker identification:
A | Fused in accordance with the manufacturer's marked rating of the system |  |  |  | Yes | TRUE | No | FALSE | N/A | FALSE
B | The primary supply is equipped with the identified disconnect means |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Adequate to meet the requirements of the system |  |  |  | Yes | TRUE | No | FALSE | N/A | FALSE
D | A short on the isolated side of each power isolation module results in a trouble condition |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Operation of a device on the source side of each shorted power isolation module is confirmed. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Power for ancillary devices is taken from a source separate from the fire alarm system control unit or transponder power supply. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Power for ancillary devices is taken from the control unit or transponder that is designed to provide such power. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Ancillary devices, which are powered from control unit or transponder, are recorded. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
Control unit or transponder location: |  |  | 0
Control unit or transponder identification: |  |  | 0
Circuit disconnect means or breaker location:
Circuit disconnect means or breaker identification:
A | Fused in accordance with the manufacturer's marked rating of the system |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | The primary supply is equipped with the identified disconnect means |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Adequate to meet the requirements of the system |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | A short on the isolated side of each power isolation module results in a trouble condition |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Operation of a device on the source side of each shorted power isolation module is confirmed. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Power for ancillary devices is taken from a source separate from the fire alarm system control unit or transponder power supply. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Power for ancillary devices is taken from the control unit or transponder that is designed to provide such power. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Ancillary devices, which are powered from control unit or transponder, are recorded. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
Control unit or transponder location: |  |  | 0
Control unit or transponder identification: |  |  | 0
Circuit disconnect means or breaker location:
Circuit disconnect means or breaker identification:
A | Fused in accordance with the manufacturer's marked rating of the system |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | The primary supply is equipped with the identified disconnect means |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Adequate to meet the requirements of the system |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | A short on the isolated side of each power isolation module results in a trouble condition |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Operation of a device on the source side of each shorted power isolation module is confirmed. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Power for ancillary devices is taken from a source separate from the fire alarm system control unit or transponder power supply. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Power for ancillary devices is taken from the control unit or transponder that is designed to provide such power. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Ancillary devices, which are powered from control unit or transponder, are recorded. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
Control unit or transponder location: |  |  | 0
Control unit or transponder identification: |  |  | 0
Circuit disconnect means or breaker location:
Circuit disconnect means or breaker identification:
A | Fused in accordance with the manufacturer's marked rating of the system |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | The primary supply is equipped with the identified disconnect means |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Adequate to meet the requirements of the system |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | A short on the isolated side of each power isolation module results in a trouble condition |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Operation of a device on the source side of each shorted power isolation module is confirmed. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Power for ancillary devices is taken from a source separate from the fire alarm system control unit or transponder power supply. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Power for ancillary devices is taken from the control unit or transponder that is designed to provide such power. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Ancillary devices, which are powered from control unit or transponder, are recorded. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE

## 22.5 ¦ Power Supply(s)
22.5 Emergency Power Supply Test and Inspection
NOTE 1 : Complete section for each control unit or transponder.
Emergency power supply location:
Emergency power supply identification:
Emergency power supply provided by:
Circuit disconnect means or breaker identification:
Batteries |  | FALSE |  |  | Generator | FALSE | UPS | FALSE | Combination |  |  | FALSE
NBC required full load alarm operation time |  |  |  |  | 2 Hours | FALSE | 1 hour | FALSE | 30 min |  | FALSE | 5 min |  | FALSE
Installed batteries Qty: |  |  | 2 | V dc: | 12V | Ah: | 20AH
BATTERY TESTS (Reference: 9.2)
A |  | Correct battery type as recommended by manufacturer. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
B |  | Correct battery rating as determined by battery calculations based on full system load. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
C |  | Battery voltage with main power supply 'ON', | [6 empty] | Voltage: |  | 27.21 |  | V dc
[9 empty] | Current: |  |  |  | A
D |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in supervisory condition. | [6 empty] | Voltage: |  | 25.48 |  | V dc
[9 empty] | Current: |  | 380 |  | A
E |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in full load alarm condition. | [6 empty] | Voltage: |  | 25.38 |  | V dc
[9 empty] | Current: |  | 1060 |  | A
F |  | Free of physical damage | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
G |  | Terminals cleaned and lubricated | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
H |  | Terminals clamped tightly. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
I |  | Correct electrolyte level. | [6 empty] | Yes | FALSE | No | FALSE | N/A | TRUE
J |  | Specific gravity of electrolyte is within manufacturer's specifications. | [6 empty] | Yes | FALSE | No | FALSE | N/A | TRUE
K |  | Battery free of electrolyte leakage. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
L |  | Adequately ventilated. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
M |  | Battery manufacturer's date code. | [6 empty] | Date: |  | 2025
N |  | Disconnection of battery causes trouble signal at the fire alarm control unit. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
O |  | Indicate type of battery tests performed:
|  | i) Required supervisory load for 24 h followed by the required full load operation; or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | ii) Silent accelerated test. (Refer to Annex C1, New Silent Accelerated Test Methods); or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | iii) Battery manufacturer's methods. (Refer to Annex C1), | [6 empty] | Yes |  | FALSE | No |  | FALSE
Specify:
P |  | Record calculated battery capacity (Refer to Annex C2.) | [6 empty] | 9.7 |  | Ah
Q |  | Record battery terminal voltage after completion of tests. | [6 empty] | 25.44 |  | V dc
R |  | Confirm battery voltage not less than 85% of its rating after the tests. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
S |  | Battery charging current | [6 empty] | 90 |  | A
EMERGENCY POWER GENERATOR TESTS (Reference: 9.3)
A | Generator provides power to the AC Circuit serving the fire alarm system. | [7 empty] | Yes | FALSE | No | FALSE | N/A | TRUE
B | Trouble condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | TRUE
C | Generator Run condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
Emergency power supply location: |  |  |  | 5th Floor West Closet
Emergency power supply identification: |  |  |  | Booster Panel
Emergency power supply provided by:
Circuit disconnect means or breaker identification:
Batteries |  | FALSE |  |  | Generator | FALSE | UPS | FALSE | Combination |  |  | FALSE
NBC required full load alarm operation time |  |  |  |  | 2 Hours | FALSE | 1 hour | FALSE | 30 min |  | FALSE | 5 min |  | FALSE
Installed batteries Qty: |  |  |  | V dc: |  | Ah:
BATTERY TESTS (Reference: 9.2)
A |  | Correct battery type as recommended by manufacturer. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
B |  | Correct battery rating as determined by battery calculations based on full system load. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
C |  | Battery voltage with main power supply 'ON', | [6 empty] | Voltage: |  | 26.68 |  | V dc
[9 empty] | Current: |  |  |  | A
D |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in supervisory condition. | [6 empty] | Voltage: |  | 25.25 |  | V dc
[9 empty] | Current: |  | 100 |  | A
E |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in full load alarm condition. | [6 empty] | Voltage: |  | 25.03 |  | V dc
[9 empty] | Current: |  | 660 |  | A
F |  | Free of physical damage | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
G |  | Terminals cleaned and lubricated | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
H |  | Terminals clamped tightly. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
I |  | Correct electrolyte level. | [6 empty] | Yes | FALSE | No | FALSE | N/A | TRUE
J |  | Specific gravity of electrolyte is within manufacturer's specifications. | [6 empty] | Yes | FALSE | No | FALSE | N/A | TRUE
K |  | Battery free of electrolyte leakage. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
L |  | Adequately ventilated. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
M |  | Battery manufacturer's date code. | [6 empty] | Date: |  | 2024
N |  | Disconnection of battery causes trouble signal at the fire alarm control unit. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
O |  | Indicate type of battery tests performed:
|  | i) Required supervisory load for 24 h followed by the required full load operation; or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | ii) Silent accelerated test. (Refer to Annex C1, New Silent Accelerated Test Methods); or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | iii) Battery manufacturer's methods. (Refer to Annex C1), | [6 empty] | Yes |  | FALSE | No |  | FALSE
Specify:
P |  | Record calculated battery capacity (Refer to Annex C2.) | [6 empty] | 2.7 |  | Ah
Q |  | Record battery terminal voltage after completion of tests. | [6 empty] | 25.22 |  | V dc
R |  | Confirm battery voltage not less than 85% of its rating after the tests. | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
S |  | Battery charging current | [6 empty] | 0-50 |  | A
EMERGENCY POWER GENERATOR TESTS (Reference: 9.3)
A | Generator provides power to the AC Circuit serving the fire alarm system. | [7 empty] | Yes | FALSE | No | FALSE | N/A | TRUE
B | Trouble condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | TRUE
C | Generator Run condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
Emergency power supply location:
Emergency power supply identification:
Emergency power supply provided by:
Circuit disconnect means or breaker identification:
Batteries |  | FALSE |  |  | Generator | FALSE | UPS | FALSE | Combination |  |  | FALSE
NBC required full load alarm operation time |  |  |  |  | 2 Hours | FALSE | 1 hour | FALSE | 30 min |  | FALSE | 5 min |  | FALSE
Installed batteries Qty: |  |  |  | V dc: |  | Ah:
BATTERY TESTS (Reference: 9.2)
A |  | Correct battery type as recommended by manufacturer. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Correct battery rating as determined by battery calculations based on full system load. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Battery voltage with main power supply 'ON', | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
D |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in supervisory condition. | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
E |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in full load alarm condition. | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
F |  | Free of physical damage | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
G |  | Terminals cleaned and lubricated | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Terminals clamped tightly. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Correct electrolyte level. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Specific gravity of electrolyte is within manufacturer's specifications. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
K |  | Battery free of electrolyte leakage. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
L |  | Adequately ventilated. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
M |  | Battery manufacturer's date code. | [6 empty] | Date:
N |  | Disconnection of battery causes trouble signal at the fire alarm control unit. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
O |  | Indicate type of battery tests performed:
|  | i) Required supervisory load for 24 h followed by the required full load operation; or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | ii) Silent accelerated test. (Refer to Annex C1, New Silent Accelerated Test Methods); or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | iii) Battery manufacturer's methods. (Refer to Annex C1), | [6 empty] | Yes |  | FALSE | No |  | FALSE
Specify:
P |  | Record calculated battery capacity (Refer to Annex C2.) | [8 empty] | Ah
Q |  | Record battery terminal voltage after completion of tests. | [8 empty] | V dc
R |  | Confirm battery voltage not less than 85% of its rating after the tests. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
S |  | Battery charging current | [8 empty] | A
EMERGENCY POWER GENERATOR TESTS (Reference: 9.3)
A | Generator provides power to the AC Circuit serving the fire alarm system. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B | Trouble condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C | Generator Run condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
Emergency power supply location:
Emergency power supply identification:
Emergency power supply provided by:
Circuit disconnect means or breaker identification:
Batteries |  | FALSE |  |  | Generator | FALSE | UPS | FALSE | Combination |  |  | FALSE
NBC required full load alarm operation time |  |  |  |  | 2 Hours | FALSE | 1 hour | FALSE | 30 min |  | FALSE | 5 min |  | FALSE
Installed batteries Qty: |  |  |  | V dc: |  | Ah:
BATTERY TESTS (Reference: 9.2)
A |  | Correct battery type as recommended by manufacturer. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Correct battery rating as determined by battery calculations based on full system load. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Battery voltage with main power supply 'ON', | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
D |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in supervisory condition. | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
E |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in full load alarm condition. | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
F |  | Free of physical damage | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
G |  | Terminals cleaned and lubricated | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Terminals clamped tightly. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Correct electrolyte level. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Specific gravity of electrolyte is within manufacturer's specifications. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
K |  | Battery free of electrolyte leakage. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
L |  | Adequately ventilated. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
M |  | Battery manufacturer's date code. | [6 empty] | Date:
N |  | Disconnection of battery causes trouble signal at the fire alarm control unit. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
O |  | Indicate type of battery tests performed:
|  | i) Required supervisory load for 24 h followed by the required full load operation; or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | ii) Silent accelerated test. (Refer to Annex C1, New Silent Accelerated Test Methods); or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | iii) Battery manufacturer's methods. (Refer to Annex C1), | [6 empty] | Yes |  | FALSE | No |  | FALSE
Specify:
P |  | Record calculated battery capacity (Refer to Annex C2.) | [8 empty] | Ah
Q |  | Record battery terminal voltage after completion of tests. | [8 empty] | V dc
R |  | Confirm battery voltage not less than 85% of its rating after the tests. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
S |  | Battery charging current | [8 empty] | A
EMERGENCY POWER GENERATOR TESTS (Reference: 9.3)
A | Generator provides power to the AC Circuit serving the fire alarm system. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B | Trouble condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C | Generator Run condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
Emergency power supply location:
Emergency power supply identification:
Emergency power supply provided by:
Circuit disconnect means or breaker identification:
Batteries |  | FALSE |  |  | Generator | FALSE | UPS | FALSE | Combination |  |  | FALSE
NBC required full load alarm operation time |  |  |  |  | 2 Hours | FALSE | 1 hour | FALSE | 30 min |  | FALSE | 5 min |  | FALSE
Installed batteries Qty: |  |  |  | V dc: |  | Ah:
BATTERY TESTS (Reference: 9.2)
A |  | Correct battery type as recommended by manufacturer. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Correct battery rating as determined by battery calculations based on full system load. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Battery voltage with main power supply 'ON', | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
D |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in supervisory condition. | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
E |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in full load alarm condition. | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
F |  | Free of physical damage | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
G |  | Terminals cleaned and lubricated | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Terminals clamped tightly. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Correct electrolyte level. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Specific gravity of electrolyte is within manufacturer's specifications. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
K |  | Battery free of electrolyte leakage. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
L |  | Adequately ventilated. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
M |  | Battery manufacturer's date code. | [6 empty] | Date:
N |  | Disconnection of battery causes trouble signal at the fire alarm control unit. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
O |  | Indicate type of battery tests performed:
|  | i) Required supervisory load for 24 h followed by the required full load operation; or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | ii) Silent accelerated test. (Refer to Annex C1, New Silent Accelerated Test Methods); or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | iii) Battery manufacturer's methods. (Refer to Annex C1), | [6 empty] | Yes |  | FALSE | No |  | FALSE
Specify:
P |  | Record calculated battery capacity (Refer to Annex C2.) | [8 empty] | Ah
Q |  | Record battery terminal voltage after completion of tests. | [8 empty] | V dc
R |  | Confirm battery voltage not less than 85% of its rating after the tests. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
S |  | Battery charging current | [8 empty] | A
EMERGENCY POWER GENERATOR TESTS (Reference: 9.3)
A | Generator provides power to the AC Circuit serving the fire alarm system. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B | Trouble condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C | Generator Run condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
Emergency power supply location:
Emergency power supply identification:
Emergency power supply provided by:
Circuit disconnect means or breaker identification:
Batteries |  | FALSE |  |  | Generator | FALSE | UPS | FALSE | Combination |  |  | FALSE
NBC required full load alarm operation time |  |  |  |  | 2 Hours | FALSE | 1 hour | FALSE | 30 min |  | FALSE | 5 min |  | FALSE
Installed batteries Qty: |  |  |  | V dc: |  | Ah:
BATTERY TESTS (Reference: 9.2)
A |  | Correct battery type as recommended by manufacturer. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Correct battery rating as determined by battery calculations based on full system load. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Battery voltage with main power supply 'ON', | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
D |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in supervisory condition. | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
E |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in full load alarm condition. | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
F |  | Free of physical damage | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
G |  | Terminals cleaned and lubricated | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Terminals clamped tightly. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Correct electrolyte level. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Specific gravity of electrolyte is within manufacturer's specifications. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
K |  | Battery free of electrolyte leakage. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
L |  | Adequately ventilated. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
M |  | Battery manufacturer's date code. | [6 empty] | Date:
N |  | Disconnection of battery causes trouble signal at the fire alarm control unit. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
O |  | Indicate type of battery tests performed:
|  | i) Required supervisory load for 24 h followed by the required full load operation; or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | ii) Silent accelerated test. (Refer to Annex C1, New Silent Accelerated Test Methods); or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | iii) Battery manufacturer's methods. (Refer to Annex C1), | [6 empty] | Yes |  | FALSE | No |  | FALSE
Specify:
P |  | Record calculated battery capacity (Refer to Annex C2.) | [8 empty] | Ah
Q |  | Record battery terminal voltage after completion of tests. | [8 empty] | V dc
R |  | Confirm battery voltage not less than 85% of its rating after the tests. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
S |  | Battery charging current | [8 empty] | A
EMERGENCY POWER GENERATOR TESTS (Reference: 9.3)
A | Generator provides power to the AC Circuit serving the fire alarm system. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B | Trouble condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C | Generator Run condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
Emergency power supply location:
Emergency power supply identification:
Emergency power supply provided by:
Circuit disconnect means or breaker identification:
Batteries |  | FALSE |  |  | Generator | FALSE | UPS | FALSE | Combination |  |  | FALSE
NBC required full load alarm operation time |  |  |  |  | 2 Hours | FALSE | 1 hour | FALSE | 30 min |  | FALSE | 5 min |  | FALSE
Installed batteries Qty: |  |  |  | V dc: |  | Ah:
BATTERY TESTS (Reference: 9.2)
A |  | Correct battery type as recommended by manufacturer. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Correct battery rating as determined by battery calculations based on full system load. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Battery voltage with main power supply 'ON', | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
D |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in supervisory condition. | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
E |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in full load alarm condition. | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
F |  | Free of physical damage | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
G |  | Terminals cleaned and lubricated | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Terminals clamped tightly. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Correct electrolyte level. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Specific gravity of electrolyte is within manufacturer's specifications. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
K |  | Battery free of electrolyte leakage. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
L |  | Adequately ventilated. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
M |  | Battery manufacturer's date code. | [6 empty] | Date:
N |  | Disconnection of battery causes trouble signal at the fire alarm control unit. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
O |  | Indicate type of battery tests performed:
|  | i) Required supervisory load for 24 h followed by the required full load operation; or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | ii) Silent accelerated test. (Refer to Annex C1, New Silent Accelerated Test Methods); or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | iii) Battery manufacturer's methods. (Refer to Annex C1), | [6 empty] | Yes |  | FALSE | No |  | FALSE
Specify:
P |  | Record calculated battery capacity (Refer to Annex C2.) | [8 empty] | Ah
Q |  | Record battery terminal voltage after completion of tests. | [8 empty] | V dc
R |  | Confirm battery voltage not less than 85% of its rating after the tests. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
S |  | Battery charging current | [8 empty] | A
EMERGENCY POWER GENERATOR TESTS (Reference: 9.3)
A | Generator provides power to the AC Circuit serving the fire alarm system. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B | Trouble condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C | Generator Run condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
Emergency power supply location:
Emergency power supply identification:
Emergency power supply provided by:
Circuit disconnect means or breaker identification:
Batteries |  | FALSE |  |  | Generator | FALSE | UPS | FALSE | Combination |  |  | FALSE
NBC required full load alarm operation time |  |  |  |  | 2 Hours | FALSE | 1 hour | FALSE | 30 min |  | FALSE | 5 min |  | FALSE
Installed batteries Qty: |  |  |  | V dc: |  | Ah:
BATTERY TESTS (Reference: 9.2)
A |  | Correct battery type as recommended by manufacturer. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Correct battery rating as determined by battery calculations based on full system load. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Battery voltage with main power supply 'ON', | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
D |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in supervisory condition. | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
E |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in full load alarm condition. | [6 empty] | Voltage: |  |  |  | V dc
[9 empty] | Current: |  |  |  | A
F |  | Free of physical damage | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
G |  | Terminals cleaned and lubricated | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Terminals clamped tightly. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Correct electrolyte level. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Specific gravity of electrolyte is within manufacturer's specifications. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
K |  | Battery free of electrolyte leakage. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
L |  | Adequately ventilated. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
M |  | Battery manufacturer's date code. | [6 empty] | Date:
N |  | Disconnection of battery causes trouble signal at the fire alarm control unit. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
O |  | Indicate type of battery tests performed:
|  | i) Required supervisory load for 24 h followed by the required full load operation; or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | ii) Silent accelerated test. (Refer to Annex C1, New Silent Accelerated Test Methods); or | [6 empty] | Yes |  | FALSE | No |  | FALSE
|  | iii) Battery manufacturer's methods. (Refer to Annex C1), | [6 empty] | Yes |  | FALSE | No |  | FALSE
Specify:
P |  | Record calculated battery capacity (Refer to Annex C2.) | [8 empty] | Ah
Q |  | Record battery terminal voltage after completion of tests. | [8 empty] | V dc
R |  | Confirm battery voltage not less than 85% of its rating after the tests. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
S |  | Battery charging current | [8 empty] | A
EMERGENCY POWER GENERATOR TESTS (Reference: 9.3)
A | Generator provides power to the AC Circuit serving the fire alarm system. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B | Trouble condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C | Generator Run condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [7 empty] | Yes | FALSE | No | FALSE | N/A | FALSE

## 22.6 ¦ Annunciator(s)
22.6 Annunciator, Remote Trouble Signal Unit, Display and Control Centre Test and Inspection
NOTE 1 : See Section 10 in CAN/ULC-S536-19
NOTE 2 : Complete section for each device
Annunciator or remote trouble signal unit location: |  | Front Door
Annunciator or remote trouble signal unit identification:
A | Power 'ON' indicator operates |  | Yes | TRUE | No | FALSE | N/A | FALSE
B | Individual alarm and supervisory zone designation labels are properly identified |  | Yes | TRUE | No | FALSE | N/A | FALSE
C | Where individual devices are annunciated confirm the individual alarm and supervisory indications are properly identified. |  | Yes | TRUE | No | FALSE | N/A | FALSE
D | Where active and supporting field devices are utilized, the device location and programmed device label/descriptor shall be confirmed. |  | Yes | TRUE | No | FALSE | N/A | FALSE
E | Common trouble signal operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
F | Visual indicator test (lamp test) operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
G | Input wiring from control unit or transponder is supervised. |  | Yes | TRUE | No | FALSE | N/A | FALSE
H | Alarm signal silence visual indicator operates. |  | Yes | TRUE | No | FALSE | N/A | FALSE
I | Switches for ancillary functions operate as per design and specification, or in accordance with documentation as detailed in Annex D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | TRUE | No | FALSE | N/A | FALSE
J | Other ancillary function visual indicators operate. |  | Yes | TRUE | No | FALSE | N/A | FALSE
K | Manual activation of alarm signal and indication operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Displays are visible in installed location. |  | Yes | TRUE | No | FALSE | N/A | FALSE
M | Operates on emergency power. |  | Yes | TRUE | No | FALSE | N/A | FALSE
Annunciator or remote trouble signal unit location:
Annunciator or remote trouble signal unit identification:
A | Power 'ON' indicator operates |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Individual alarm and supervisory zone designation labels are properly identified |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Where individual devices are annunciated confirm the individual alarm and supervisory indications are properly identified. |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | Where active and supporting field devices are utilized, the device location and programmed device label/descriptor shall be confirmed. |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Common trouble signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Visual indicator test (lamp test) operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Input wiring from control unit or transponder is supervised. |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alarm signal silence visual indicator operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | I Switches for ancillary functions operate as per design and specification, or in accordance with documentation as detailed in Annex D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Other ancillary function visual indicators operate. |  | Yes | FALSE | No | FALSE | N/A | FALSE
K | Manual activation of alarm signal and indication operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Displays are visible in installed location. |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Operates on emergency power. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Annunciator or remote trouble signal unit location:
Annunciator or remote trouble signal unit identification:
A | Power 'ON' indicator operates |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Individual alarm and supervisory zone designation labels are properly identified |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Where individual devices are annunciated confirm the individual alarm and supervisory indications are properly identified. |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | Where active and supporting field devices are utilized, the device location and programmed device label/descriptor shall be confirmed. |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Common trouble signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Visual indicator test (lamp test) operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Input wiring from control unit or transponder is supervised. |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alarm signal silence visual indicator operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | I Switches for ancillary functions operate as per design and specification, or in accordance with documentation as detailed in Annex D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Other ancillary function visual indicators operate. |  | Yes | FALSE | No | FALSE | N/A | FALSE
K | Manual activation of alarm signal and indication operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Displays are visible in installed location. |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Operates on emergency power. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Annunciator or remote trouble signal unit location:
Annunciator or remote trouble signal unit identification:
A | Power 'ON' indicator operates |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Individual alarm and supervisory zone designation labels are properly identified |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Where individual devices are annunciated confirm the individual alarm and supervisory indications are properly identified. |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | Where active and supporting field devices are utilized, the device location and programmed device label/descriptor shall be confirmed. |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Common trouble signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Visual indicator test (lamp test) operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Input wiring from control unit or transponder is supervised. |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alarm signal silence visual indicator operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | I Switches for ancillary functions operate as per design and specification, or in accordance with documentation as detailed in Annex D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Other ancillary function visual indicators operate. |  | Yes | FALSE | No | FALSE | N/A | FALSE
K | Manual activation of alarm signal and indication operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Displays are visible in installed location. |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Operates on emergency power. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Annunciator or remote trouble signal unit location:
Annunciator or remote trouble signal unit identification:
A | Power 'ON' indicator operates |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Individual alarm and supervisory zone designation labels are properly identified |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Where individual devices are annunciated confirm the individual alarm and supervisory indications are properly identified. |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | Where active and supporting field devices are utilized, the device location and programmed device label/descriptor shall be confirmed. |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Common trouble signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Visual indicator test (lamp test) operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Input wiring from control unit or transponder is supervised. |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alarm signal silence visual indicator operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | I Switches for ancillary functions operate as per design and specification, or in accordance with documentation as detailed in Annex D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Other ancillary function visual indicators operate. |  | Yes | FALSE | No | FALSE | N/A | FALSE
K | Manual activation of alarm signal and indication operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Displays are visible in installed location. |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Operates on emergency power. |  | Yes | FALSE | No | FALSE | N/A | FALSE

## 22.7 ¦ Annun & Seq Disp
22.7 Annunciator or Sequential Display
NOTE 1 : See 10.2 in CAN/ULC-S536-19
NOTE 2 : If the fire alarm system DOES utilize remote annunciators, complete 22.7 for each annunciator or sequential display
|  | There are no annunciators or sequential displays on this system. | TRUE
Annunciator or sequential display location:
Annunciator or sequential display identification:
A | Power 'ON' indicator operates. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Individual alarm and supervisory zone designation labels are properly identified. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Where individual devices are also annunciated confirm the individual alarm and supervisory indications are properly identified. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | Where active and supporting field devices are utilized, the device location and programmed device label/descriptor shall be confirmed. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Common trouble signal operates. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Visual indicator test (lamp test) operates. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Input wiring from control unit or transponder is supervised. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alarm signal silence visual indicator operates. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Switches for ancillary functions operate as per design and specification, or in accordance with documentation as detailed in Section 21. (See section 7.) |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Ancillary function visual indicators operate. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
K | Manual activation of alarm signal and indication operates. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Displays are visible in installed location. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Multi-line sequential display operates as per 10.2, where utilized. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
22.8 Remote Trouble Signal Unit Test and Inspection
NOTE : If the fire alarm system DOES utilize remote trouble signal unit, complete 22.8 for each remote trouble signal unit
|  | There are no remote trouble signal units on this system. | TRUE
Remote trouble signal unit location:
Remote trouble signal unit identification:
A | Input wiring from control unit or transponder is supervised. |  |  | Yes |  | FALSE | No |  | FALSE
B | Visual trouble signal operates. |  |  | Yes |  | FALSE | No |  | FALSE
C | Audible trouble signal operates. |  |  | Yes |  | FALSE | No |  | FALSE
D | Audible trouble signal silence operates. |  |  | Yes |  | FALSE | No |  | FALSE
Annunciator or sequential display location:
Annunciator or sequential display identification:
A | Power 'ON' indicator operates. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Individual alarm and supervisory zone designation labels are properly identified. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Where individual devices are also annunciated confirm the individual alarm and supervisory indications are properly identified. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | Where active and supporting field devices are utilized, the device location and programmed device label/descriptor shall be confirmed. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Common trouble signal operates. |  |  | Yes | FALSE | No | FALSE
F | Visual indicator test (lamp test) operates. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Input wiring from control unit or transponder is supervised. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alarm signal silence visual indicator operates. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Switches for ancillary functions operate as per design and specification, or in accordance with documentation as detailed in Section 21. (See section 7.) |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Ancillary function visual indicators operate. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
K | Manual activation of alarm signal and indication operates. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Displays are visible in installed location. |  |  | Yes | FALSE | No | FALSE
M | Multi-line sequential display operates as per 10.2, where utilized. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
Remote trouble signal unit location:
Remote trouble signal unit identification:
A | Input wiring from control unit or transponder is supervised. |  |  | Yes |  | FALSE | No |  | FALSE
B | Visual trouble signal operates. |  |  | Yes |  | FALSE | No |  | FALSE
C | Audible trouble signal operates. |  |  | Yes |  | FALSE | No |  | FALSE
D | Audible trouble signal silence operates. |  |  | Yes |  | FALSE | No |  | FALSE
Annunciator or sequential display location:
Annunciator or sequential display identification:
A | Power 'ON' indicator operates. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Individual alarm and supervisory zone designation labels are properly identified. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Where individual devices are also annunciated confirm the individual alarm and supervisory indications are properly identified. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | Where active and supporting field devices are utilized, the device location and programmed device label/descriptor shall be confirmed. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Common trouble signal operates. |  |  | Yes | FALSE | No | FALSE
F | Visual indicator test (lamp test) operates. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Input wiring from control unit or transponder is supervised. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alarm signal silence visual indicator operates. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Switches for ancillary functions operate as per design and specification, or in accordance with documentation as detailed in Section 21. (See section 7.) |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Ancillary function visual indicators operate. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
K | Manual activation of alarm signal and indication operates. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Displays are visible in installed location. |  |  | Yes | FALSE | No | FALSE
M | Multi-line sequential display operates as per 10.2, where utilized. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
Remote trouble signal unit location:
Remote trouble signal unit identification:
A | Input wiring from control unit or transponder is supervised. |  |  | Yes |  | FALSE | No |  | FALSE
B | Visual trouble signal operates. |  |  | Yes |  | FALSE | No |  | FALSE
C | Audible trouble signal operates. |  |  | Yes |  | FALSE | No |  | FALSE
D | Audible trouble signal silence operates. |  |  | Yes |  | FALSE | No |  | FALSE

## 22.9 + 22.10 ¦ Monitoring Etc.
22.9 Printer Test
NOTE: If the fire alarm system DOES utilize printers, complete 22.9 for each printer unit.
|  |  |  | There are no printers on this system | TRUE
Printer location :
Printer identification :
A | Operates as per design and specification, or in accordance with documentation as detailed in Annex D, Description of Fire Alarm System for Inspection and Test Procedures. | [6 empty] | Yes |  | FALSE | No |  | FALSE
B | Zone of each alarm initiating device is correctly printed | [6 empty] | Yes |  | FALSE | No |  | FALSE
22.10 Ancillary Device Circuit Test
Specific type of ancillary circuit |  | Ancillary circuit powered by : |  | Operation of ancillary circuit confirmed |  |  |  | Method of confirmation See Annex A, A22.10
|  | FACU* Check if applicable | Others specify
DOOR HOLDERS |  | FALSE |  | Yes | TRUE | No | FALSE
FAN SHUTDOWN |  | FALSE |  | Yes | TRUE | No | FALSE
PRESSURIZATION FANS |  | FALSE |  | Yes | TRUE | No | FALSE
ELEVATOR HOMING |  | FALSE |  | Yes | TRUE | No | FALSE
ELEVATOR ALT. HOMING |  | FALSE |  | Yes | TRUE | No | FALSE
|  | FALSE |  | Yes | FALSE | No | FALSE
*FACU - fire alarm control unit
NOTE: The tests reported on this Form may not include the actual operational test of ancillary devices, except when noted in the Method of Confirmation column. See Annex A, A22.10.
22.11 Interconnection to the Fire Signal Receiving Centre
NOTE: If the fire alarm system DOES have an interconnection to the fire signal receiving centre, complete 22.11 for each transmitter.
[6 empty] | There are no interconnections to a Fire Signal Receiving Centre on this system. | FALSE
A | The fire signal receiving centre transmitter is integral to the fire alarm control unit. | [6 empty] | Yes |  | FALSE | No |  | TRUE
B | Receipt of the alarm transmission to the fire signal receiving centre. | [6 empty] | Yes |  | TRUE | No |  | FALSE
C | Receipt of the supervisory transmission to the fire signal receiving centre | [6 empty] | Yes | TRUE | No | FALSE | N/A | FALSE
D | Receipt of the trouble transmission to the fire signal receiving centre | [6 empty] | Yes |  | TRUE | No |  | FALSE
E | Disabling or disconnecting the fire signal receiving centre transmitter results in a specific trouble signal at the control unit or transmitter and also transmits a trouble signal to the fire signal receiving centre. | [6 empty] | Yes |  | FALSE | No |  | FALSE
F | Disabling or disconnecting the fire signal receiving centre transmitter transmits a trouble signal to the fire signal receiving centre. | [6 empty] | Yes |  | FALSE | No |  | FALSE
G | Record the company name and telephone number of the fire signal receiving centre. | [6 empty] | Name : |  | Tyco
[8 empty] | Telephone : |  | 1-800-289-2647
H | Operation of the fire signal receiving centre disconnect means transmits trouble to the fire signal receiving centre. | [6 empty] | Yes |  | FALSE | No |  | FALSE | TRUE

## 23.1 Field Device Legend
23 Field Device Records
23.1 Field Device Testing – Legend and Notes
NOTE: Add additional line items for each additional type and/or model number of devices forming part of the fire alarm system as necessary to this Legend
Device type | Description |  |  | Type | Model no.
M | Manual Station |  |  | EDWARDS | 270 GAO/271/272/273
RHT | Heat Detector, Restorable |  |  | EDWARDS | SIGA2- HRS
HT | Heat Detector, Non-Restorable
S | Smoke Detector
| Sensitivity Test Method or Test Equipment: |  |  | Not applicable | Not applicable
| Model/Method: | EDWARDS
| Manufacturer Sensitivity Range: |  | SIGA2-PS | Not applicable | Not applicable
Note: CAN/ULC-S529 required range is 0.5 to 4.0 %/ft obscuration. Recorded sensitivity measurement units may not be in %/ft depending upon the testing method used.
SB | Sounder Base
RI | Remote Indicator Unit
DS | Duct Smoke detector
-- | Other Type of Detector |  |  | TS | B'FLY
SFD | Supporting Field Device (Monitor)
FS | Sprinkler Flow Switch |  |  | EDWARDS | SIGA-CT
SS | Sprinkler Supervisory device
-- | Other Supervisory Devices (Low Pressure, Low Water, Low Temperature, Power Loss, etc.) |  |  | TS | B'FLY
EM | Fault Isolator
B | Bell
BZ | Suite Buzzer
H | Horn |  |  | EDWARDS | 682-1C/EG1RF-HD
V | Visible Signal Device
SP | Cone Type Speaker
HSP | Horn Type Speaker
SSS | Suite Silence Switch
SSAD | Suite Silence Audible Device
AD | Ancillary Device |  |  |  | SIGA-CR
ET | Emergency Telephone
EOL | End-of-Line Device
NOTE: Refer to Section 14, Field Devices.
Notes continue onto next page…
23.1.1 The following notes apply to 23.2, Individual Device Record
NOTE 1: | Smoke detector sensitivity reading confirmed by the control panel or measurement obtained through testing to be recorded in the measurements column
NOTE 2: | Smoke detector cleaning or replacement date should also be recorded in the comments column.
NOTE 3: | Status change, including time delay, should be recorded in the measurements column.
NOTE 4: | Duct smoke detector pressure differential should be confirmed and recorded in the measurements column.
NOTE 5: | Transport time of air sampling type detector to be confirmed and recorded in the measurements column
NOTE 6: | Time delay setting of water flow switch should be recorded in the measurements column.
NOTE 7: | Sprinkler supervisory switches cause supervisory condition to be annunciated but not an alarm condition.
NOTE 8: | Upper and lower pressure setting of supervisory devices should be recorded in the measurements column.
NOTE 9: | Low temperature setting should be recorded in the measurements column.
NOTE 10: | Identify the specific ancillary devices in the measurements column.
NOTE 11: | Identify date field device operation (e.g., alarm, trouble, supervisory, annunciation indication).
NOTE 12: | Identify zone, circuit number, or address.
NOTE 13: | Identify conventional field device locations.
NOTE 14: | Identify active field device and supporting field device, data communication link (DCL), address and location.
NOTE 15: | a) Test and confirm conventional field device supervision of wiring via open circuit fault
b) Test and confirm active and supporting field device supervision via absence of device.
NOTE 16: | Confirm field device free of damage.
NOTE 17: | Confirm field device free of foreign substance.
NOTE 18: | Confirm field device mechanically supported independently of the wiring.
NOTE 19: | Confirm field device protective dust shields or covers removed.
NOTE 20: | "Correctly installed" refers to the Version of CAN/ULC-S524, Standard for the Installation for Fire Alarm Systems, applicable at the time of installation of the system or device being tested.
NOTE 21: | Smoke Detectors that employ sounder bases or activate local audible signaling device(s), used in lieu of smoke alarms, to be tested to confirm local sounder operation and annunciation at the control panel, including visible device operation, as applicable, and individually recorded.
NOTE 22: | When batteries are replaced in the short-range radio frequency (wireless) devices, battery replacement date to be identified in the comments section.

## 23.2 Device Record
Section 33.2 Individual Device Record
NOTE: Device type can be expressed as an abbreviation per 23.1, Field Device Testing - Legend and Notes.
NOTE: All Sprinkler Devices, please refer to the Sprinkler System Report
Building Name: | The Q Apartments | [8 empty] | Date (DD/MMM/YYYY): | May 21 - 23, 2025
Additional Device Legend for devices not included in Section 23.1 Field Device Legend of CAN/ULC S536-19
BZB: Sounder Base |  | GA: General Alarm | LA: Low Air Signal |  |  | DH: Door Holder | [5 empty] | RI: Remote Indicator
H/V: Horn Strobe Combo |  | ISO: Isolator | PL: Power Loss |  |  | FHT: Fixed Temp Heat Detector | [5 empty] | S/CO: Smoke/CO Combo Detector
SP: Cone Type Speaker |  | RHT/S: Heat/Smoke Detector Combo | TS: Tamper Switch |  |  | HHT: High Heat Detector (Non-Rest.) | [5 empty] | ISO: Isolator (A: Audible, D: Data Loop)
MOD: Module (R, 2, R6, 10, M, CR) |  | RI: Remote Indicator | SW: Silencing Switch |  |  | AD: Ancillary Device | [5 empty] | SA + (Add ons): Smoke Alarms
Device Location |  | Annunciated Device Label/LCD Text (If applicable) | Device Type (or abbreviation) | Requires Service or Missing | Circuit Number or Device Address | Annunciated FIRE ZONE | Correctly Installed (Y/N) | Measurements (Smoke Alarm Due Dates) | Alarm/Activation Confirmed | Annunciator Indication | Supervised Circuit Trouble Signal | General Alarm Circuit (if applicable) | Remarks |  |  |  | Fire Alarm Device Look Up Table
MONITORING COMPANY |  |  | TYCO | [10 empty] | DATA VALIDATION |  |  | R (Device Type) | AA (G Output) | AB (I Output) | AC (J Output) | AD (K Output)
MONITORING FIRE |  |  | YES | [10 empty] | ✔ | Y | YES | M | Y | ✔ | ✔ | ✔
MONITORING TROUBLE |  |  | YES | [10 empty] | ✖ | N | - | RHT | Y | ✔ | ✔ | ✔
MONITORING SUPERVISION |  |  | YES | [10 empty] | N/A | - |  | HT | Y | ✔ | ✔ | ✔
DOOR HOLDERS |  |  | YES | [10 empty] | TO |  |  | S | Y | ✔ | ✔ | ✔
FAN SHUT DOWN |  |  | YES | [10 empty] | - |  |  | SB | Y | ✔ | ✔ | ✔
PRESSURIZATION FANS |  |  | YES | [13 empty] | RI | Y | ✔ | ✔ | ✔
MAGNETIC LOCKS |  |  | NONE | [13 empty] | DS | Y | ✔ | ✔ | ✔
ELEVATOR HOMING |  |  | YES | [13 empty] | SFD | Y |  | ✔ | ✔
ELEVATOR ALT HOMING |  |  | YES | [9 empty] | ALT Floor Basement |  |  |  | FS | Y | ✔ | ✔ | ✔
[17 empty] | SS | Y | ✔ | ✔ | ✔
[17 empty] | EM | Y | ✔ | ✔ | ✔
[17 empty] | B | Y | ✔ | ✔ | ✔
Parkade Electrical Room |  |  | PANEL | YES |  |  | Y |  | ✔ | ✔ |  |  | Active trouble - See deficiency summary |  |  |  | H | Y | ✔ | ✔ | ✔
Parkade Electrical Room |  |  | BATT |  |  |  | Y |  | ✔ |  |  |  | Replaced 2025 |  |  |  | V | Y | ✔ | ✔ | ✔
[17 empty] | SP | Y | ✔ | ✔ | ✔
[17 empty] | HSP | Y | ✔ | ✔ | ✔
5th Floor West Closet by Elevator |  |  | BOOSTER | [9 empty] | Lock difficult to open |  |  |  | SSS | Y | ✔ | ✔ | ✔
5th Floor West Closet by Elevator |  |  | BATT |  |  |  | Y |  | ✔ |  |  |  | Replaced 2024 |  |  |  | SSAD | Y | ✔ | ✔ | ✔
[17 empty] | AD | Y | ✔ | ✔ | ✔
[17 empty] | ET | Y | ✔ | ✔ | ✔
Front Door |  |  | ANNUN |  |  |  | Y |  | ✔ | ✔ | [6 empty] | EOL | Y
[17 empty] | RHT/S | Y | ✔ | ✔ | ✔
[17 empty] | BZ | Y | ✔ | ✔ | ✔
ROOF | [16 empty] | H/V | Y | ✔ | ✔ | ✔
West Roof |  |  | DS |  |  | 24 | Y |  | ✔ | ✔ | ✔ |  | SIGA-SD |  |  |  | SP | Y | ✔ | ✔ | ✔
West Roof MUA 2 |  |  | RELAY |  |  | 24 | [6 empty] | MUA Shutdown Relay |  |  |  | DH | Y | ✔ | ✔ | ✔
[17 empty] | FHT | Y | ✔ | ✔ | ✔
East Roof |  |  | DS |  |  | 25 | Y |  | ✔ | ✔ | ✔ |  | SIGA-SD |  |  |  | GA | Y | ✔ | ✔ | ✔
East Roof MUA-1 |  |  | RELAY |  |  | 25 | [6 empty] | MUA Shutdown Relay |  |  |  | HHT | Y | ✔ | ✔ | ✔
[17 empty] | MAG | Y | ✔ | ✔ | ✔ | SA","SAA" "SAAB","SAB", "SAPA" SAPAB","SAPB","SACOA","SACOB","SACOAB", "SAPCOA", "SAPCOB","SAPCOB","SAPCOAB","
[17 empty] | MOD-R | Y | ✔ | ✔ | ✔ | SAA | SACOA | SALi | SAAR | SAPCOLi | SAPALiV
[17 empty] | MOD-2 | Y | ✔ | ✔ | ✔ | SAAB | SACOB | SAALi | SAABR | SACOALi | SAALiV
[17 empty] | MOD-R6 | Y | ✔ | ✔ | ✔ | SAB | SACOAB | SAPLi | SAPABR |  | SAAV
[17 empty] | MOD | Y | ✔ | ✔ | ✔ | SAPA | SAPCOA |  |  |  | SAPAV
[17 empty] | SFD | Y | ✔ | ✔ | ✔ | SAPAB | SAPCOAB |  |  |  | SAPABV
[17 empty] | LA | Y | ✔ | ✔ | ✔ | SAPB | SAPCOB |  |  |  | SAABV
[17 empty] | TS | Y | ✔ | ✔ | ✔
[17 empty] | ISO | Y
8TH FLOOR | [16 empty] | ISO-A | Y |  |  |  | SALi", "SAALi","SAPLi","SAAR","SAPABR","SAABR","SAPCOLi" "SACOALi" "SAALiV","SAPALiV","SAAV","SAPAV","SAPABV","SAABV"
801 |  |  | RHT |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | ISO-D | Y
801 |  |  | H |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | SAPB | Y | ✔ |  |  | BASE | IF CO | IF RELAY ADDED | IF STROBE
801 |  |  | SAAB |  |  |  | Y | 2031 | ✔ | [7 empty] | SAB | Y | ✔ |  |  | SAA | SACOA | SAAR | SAAV
801 |  |  | SAAB |  |  |  | Y | 2031 | ✔ | [7 empty] | SAA | Y | ✔ |  |  | SAAB | SACOAB | SAABR | SAABV
801 |  |  | SAAB |  |  |  | Y | 2031 | ✔ | [7 empty] | SAAB | Y | ✔ |  |  | SAPA | SAPCOA | SAPAR | SAPAV
[17 empty] | SAPA | Y | ✔ |  |  | SAPAB | SAPCOAB | SAPABR | SAPABV
802 |  |  | RHT |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | SAPAB | Y | ✔ |  |  | SALi | SACOALi
802 |  |  | H |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | SALi | Y | ✔ |  |  | SAALi | SAPCOLi |  | SAALiV
802 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement |  |  |  | SAALi | Y | ✔ |  |  | SAPLi
802 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement |  |  |  | SAPLi | Y | ✔ |  |  | SAPALi |  |  | SAPALiV
802 |  |  | SAAB |  |  |  | Y | 2027 | ✔ | [7 empty] | SAPALi | Y | ✔
[17 empty] | SACOA | Y | ✔
803 |  |  | RHT |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | SACOAB | Y | ✔
803 |  |  | H |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | SAPCOA | Y | ✔
803 |  |  | SAAB |  |  |  | Y | 2027 | ✔ | [7 empty] | SAPCOAB | Y | ✔
[17 empty] | SACOALi | Y | ✔
804 |  |  | RHT |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | SAPCOLi | Y | ✔
804 |  |  | H |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | SAAR | Y | ✔
804 |  |  | SAAB |  |  |  | Y | 2030 | ✔ | [7 empty] | SAABR | Y | ✔
[17 empty] | SAPAR | Y | ✔
805 |  |  | RHT |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | SAPABR | Y | ✔
805 |  |  | H |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | SAAV | Y | ✔
805 |  |  | SAAB |  |  |  | Y | 2036 | ✔ | [7 empty] | SAABV | Y | ✔
[17 empty] | SAPAV | Y | ✔
815 |  |  | RHT |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | SAPABV | Y | ✔
815 |  |  | H |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | SAALiV | Y | ✔
815 |  |  | SAAB |  |  |  | Y | 2030 | ✔ | [7 empty] | SAPALiV | Y | ✔
[17 empty] | SALi | Y | ✔
816 |  |  | RHT |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | SAALi | Y | ✔
816 |  |  | H |  |  | 21 | Y |  | ✔ | ✔ | ✔ | [5 empty] | SAPLi | Y | ✔
816 |  |  | SAAB |  |  |  | Y | 2036 | ✔ | [7 empty] | SAPCOB | Y | ✔
816 |  |  | SAAB |  |  |  | Y | 2036 | ✔ | [7 empty] | PANEL | Y | ✔ | ✔
[17 empty] | BATT | Y | ✔
806 |  |  | RHT |  |  | 9 | Y |  | ✔ | ✔ | ✔ | [5 empty] | ANNUN | Y | ✔ | ✔
806 |  |  | H |  |  | 9 | Y |  | ✔ | ✔ | ✔
806 |  |  | SAAB |  |  |  | Y | 2036 | ✔
807 |  |  | RHT |  |  | 9 | Y |  | ✔ | ✔ | ✔
807 |  |  | H |  |  | 9 | Y |  | ✔ | ✔ | ✔
807 |  |  | SAAB |  |  |  | Y | 2036 | ✔
808 |  |  | RHT |  |  | 9 | Y |  | ✔ | ✔ | ✔
808 |  |  | H |  |  | 9 | Y |  | ✔ | ✔ | ✔
808 |  |  | SAAB |  |  |  | Y | 2033 | ✔
812 |  |  | RHT |  |  | 9 | Y |  | ✔ | ✔ | ✔
812 |  |  | H |  |  | 9 | Y |  | ✔ | ✔ | ✔
812 |  |  | SAAB |  |  |  | Y | 2036 | ✔
813 |  |  | RHT |  |  | 9 | Y |  | ✔ | ✔ | ✔
813 |  |  | H |  |  | 9 | Y |  | ✔ | ✔ | ✔
813 |  |  | SAAB |  |  |  | Y | 2036 | ✔
811 |  |  | RHT |  |  | 9 | Y |  | ✔ | ✔ | ✔
811 |  |  | H |  |  | 9 | Y |  | ✔ | ✔ | ✔
811 |  |  | H |  |  | 9 | Y |  | ✔ | ✔ | ✔
811 |  |  | SAAB |  |  |  | Y | 2036 | ✔
811 |  |  | SAAB |  |  |  | Y | 2027 | ✔
811 |  |  | SAAB |  |  |  | Y | 2032 | ✔
809 |  |  | RHT |  |  | 9 | Y |  | ✔ | ✔ | ✔
809 |  |  | H |  |  | 9 | Y |  | ✔ | ✔ | ✔
809 |  |  | SAAB |  |  |  | Y | 2032 | ✔
810 |  |  | RHT |  |  | 9 | Y |  | ✔ | ✔ | ✔
810 |  |  | H |  |  | 9 | Y |  | ✔ | ✔ | ✔
810 |  |  | H |  |  | 9 | Y |  | ✔ | ✔ | ✔
810 |  |  | H |  |  | 9 | Y |  | ✔ | ✔ | ✔
810 |  |  | SAAB |  |  |  | Y | 2032 | ✔
810 |  |  | SAAB |  |  |  | Y | 2032 | ✔
810 |  |  | SAAB |  |  |  | Y | 2032 | ✔
814 |  |  | RHT |  |  | 9 | Y |  | ✔ | ✔ | ✔
814 |  |  | H |  |  | 9 | Y |  | ✔ | ✔ | ✔
814 |  |  | SAAB |  |  |  | Y | 2036 | ✔
7TH FLOOR
707 |  |  | RHT |  |  | 8 | Y |  | ✔ | ✔ | ✔
707 |  |  | H |  |  | 8 | Y |  | ✔ | ✔ | ✔
707 |  |  | SAAB |  |  |  | Y | 2026 | ✔
708 |  |  | RHT |  |  | 8 | Y |  | ✔ | ✔ | ✔
708 |  |  | H |  |  | 8 | Y |  | ✔ | ✔ | ✔
708 |  |  | SAAB |  |  |  | Y | 2031 | ✔
709 |  |  | RHT |  |  | 8 | Y |  | ✔ | ✔ | ✔
709 |  |  | H |  |  | 8 | Y |  | ✔ | ✔ | ✔
709 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
710 |  |  | RHT |  |  | 8 | Y |  | ✔ | ✔ | ✔
710 |  |  | H |  |  | 8 | Y |  | ✔ | ✔ | ✔
710 |  |  | SAAB |  |  |  | Y | 2034 | ✔
714 |  |  | RHT |  |  | 8 | Y |  | ✔ | ✔ | ✔
714 |  |  | H |  |  | 8 | Y |  | ✔ | ✔ | ✔
714 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
715 |  |  | RHT |  |  | 8 | Y |  | ✔ | ✔ | ✔
715 |  |  | H |  |  | 8 | Y |  | ✔ | ✔ | ✔
715 |  |  | SAAB |  |  |  | Y | 2031 | ✔
716 |  |  | RHT |  |  | 8 | Y |  | ✔ | ✔ | ✔
716 |  |  | H |  |  | 8 | Y |  | ✔ | ✔ | ✔
716 |  |  | SAAB |  |  |  | Y | 2031 | ✔
712 |  |  | RHT |  |  | 8 | Y |  | ✔ | ✔ | ✔
712 |  |  | RHT |  |  | 8 | Y |  | ✔ | ✔ | ✔
712 |  |  | H |  |  | 8 | Y |  | ✔ | ✔ | ✔
712 |  |  | SAAB |  |  |  | Y | 2030 | ✔
712 |  |  | SAAB |  |  |  | Y | 2030 | ✔
712 |  |  | SAAB |  |  |  | Y | 2030 | ✔
713 |  |  | RHT |  |  | 8 | Y |  | ✔ | ✔ | ✔
713 |  |  | H |  |  | 8 | Y |  | ✔ | ✔ | ✔
713 |  |  | H |  |  | 8 | Y |  | ✔ | ✔ | ✔
713 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
713 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
713 |  |  | SAAB |  |  |  | Y | 2031 | ✔
713 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
711 |  |  | RHT |  |  | 8 | Y |  | ✔ | ✔ | ✔
711 |  |  | H |  |  | 8 | Y |  | ✔ | ✔ | ✔
711 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
701 |  |  | RHT |  |  | 20 | Y |  | ✔ | ✔ | ✔
701 |  |  | H |  |  | 20 | Y |  | ✔ | ✔ | ✔
701 |  |  | SAAB |  |  |  | Y | 2027 | ✔
701 |  |  | SAAB |  |  |  | Y | 2027 | ✔
702 |  |  | RHT |  |  | 20 | Y |  | ✔ | ✔ | ✔
702 |  |  | H |  |  | 20 | Y |  | ✔ | ✔ | ✔
702 |  |  | SAAB |  |  |  | Y | 2028 | ✔
703 |  |  | RHT |  |  | 20 | Y |  | ✔ | ✔ | ✔
703 |  |  | H |  |  | 20 | Y |  | ✔ | ✔ | ✔
703 |  |  | SAAB |  |  |  | Y | 2026 | ✔
704 |  |  | RHT |  |  | 20 | Y |  | ✔ | ✔ | ✔
704 |  |  | H |  |  | 20 | Y |  | ✔ | ✔ | ✔
704 |  |  | SAAB |  |  |  | Y | 2027 | ✔
704 |  |  | SAAB |  |  |  | Y | 2027 | ✔
704 |  |  | SAAB |  |  |  | Y | 2027 | ✔
705 |  |  | RHT |  |  | 20 | Y |  | ✔ | ✔ | ✔
705 |  |  | H |  |  | 20 | Y |  | ✔ | ✔ | ✔
705 |  |  | SAAB |  |  |  | Y | 2030 | ✔
706 |  |  | RHT |  |  | 20 | Y |  | ✔ | ✔ | ✔
706 |  |  | H |  |  | 20 | Y |  | ✔ | ✔ | ✔
706 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
718 |  |  | RHT |  |  | 20 | Y |  | ✔ | ✔ | ✔
718 |  |  | H |  |  | 20 | Y |  | ✔ | ✔ | ✔
718 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
718 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
717 |  |  | RHT |  |  | 20 | Y |  | ✔ | ✔ | ✔
717 |  |  | H |  |  | 20 | Y |  | ✔ | ✔ | ✔
717 |  |  | SAAB |  |  |  | Y | 2026 | ✔
6TH FLOOR
611 |  |  | RHT |  |  | 7 | Y |  | ✔ | ✔ | ✔
611 |  |  | H |  |  | 7 | Y |  | ✔ | ✔ | ✔
611 |  |  | SAALi |  |  |  | Y | 2030 | ✔
612 |  |  | RHT |  |  | 7 | Y |  | ✔ | ✔ | ✔
612 |  |  | H |  |  | 7 | Y |  | ✔ | ✔ | ✔
612 Lounge |  |  | RHT |  |  | 7 | Y |  | ✔ | ✔ | ✔
612 Hall |  |  | SAALi |  |  |  | Y | 2030 | ✔
612 Master Bedroom |  |  | SAALi |  |  |  | Y | 2030 | ✔
612 |  |  | SAAB |  |  |  | Y | 2031 | ✔
610 |  |  | RHT |  |  | 7 | Y |  | ✔ | ✔ | ✔
610 |  |  | H |  |  | 7 | Y |  | ✔ | ✔ | ✔
610 |  |  | SAALi |  |  |  | Y | 2030 | ✔
614 |  |  | RHT |  |  | 7 | Y |  | ✔ | ✔ | ✔
614 |  |  | H |  |  | 7 | Y |  | ✔ | ✔ | ✔
614 |  |  | SAAB |  |  |  | Y | 2034 | ✔
615 |  |  | RHT |  |  | 7 | Y |  | ✔ | ✔ | ✔
615 |  |  | H |  |  | 7 | Y |  | ✔ | ✔ | ✔
615 |  |  | SAAB |  |  |  | Y | 2034 | ✔
609 |  |  | RHT |  |  | 7 | Y |  | ✔ | ✔ | ✔
609 |  |  | H |  |  | 7 | Y |  | ✔ | ✔ | ✔
609 |  |  | SAB |  |  |  | Y | 2028 | ✔
613 |  |  | RHT |  |  | 7 | Y |  | ✔ | ✔ | ✔
613 |  |  | H |  |  | 7 | Y |  | ✔ | ✔ | ✔
613 |  |  | H |  |  | 7 | Y |  | ✔ | ✔ | ✔
613 Hall |  |  | SAAB |  |  |  | Y | 2030 | ✔
613 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
613 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
613 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
616 |  |  | RHT |  |  | 7 | Y |  | ✔ | ✔ | ✔
616 |  |  | H |  |  | 7 | Y |  | ✔ | ✔ | ✔
616 |  |  | SAA |  |  |  | Y | 2030 | ✔
608 |  |  | RHT |  |  | 7 | Y |  | ✔ | ✔ | ✔
608 |  |  | H |  |  | 7 | Y |  | ✔ | ✔ | ✔
608 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
607 |  |  | RHT |  |  | 7 | Y |  | ✔ | ✔ | ✔
607 |  |  | H |  |  | 7 | Y |  | ✔ | ✔ | ✔
607 |  |  | SAAB |  |  |  | Y | 2029 | ✔
617 |  |  | RHT |  |  | 19 | Y |  | ✔ | ✔ | ✔
617 |  |  | H |  |  | 19 | Y |  | ✔ | ✔ | ✔
617 |  |  | SAAB |  |  |  | Y | 2027 | ✔
606 |  |  | RHT |  |  | 19 | Y |  | ✔ | ✔ | ✔
606 |  |  | H |  |  | 19 | Y |  | ✔ | ✔ | ✔
606 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
618 |  |  | RHT |  |  | 19 | Y |  | ✔ | ✔ | ✔
618 |  |  | H |  |  | 19 | Y |  | ✔ | ✔ | ✔
618 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
618 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
605 |  |  | RHT |  |  | 19 | Y |  | ✔ | ✔ | ✔
605 |  |  | H |  |  | 19 | Y |  | ✔ | ✔ | ✔
605 |  |  | SAAB |  |  |  | Y | 2028 | ✔
601 |  |  | RHT |  |  | 19 | Y |  | ✔ | ✔ | ✔
601 |  |  | H |  |  | 19 | Y |  | ✔ | ✔ | ✔
601 |  |  | SAAB |  |  |  | Y | 2027 | ✔
601 Hall |  |  | SAAB |  |  |  | Y | 2027 | ✔
602 |  |  | RHT |  |  | 19 | Y |  | ✔ | ✔ | ✔
602 |  |  | H |  |  | 19 | Y |  | ✔ | ✔ | ✔
602 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
604 |  |  | RHT |  |  | 19 | Y |  | ✔ | ✔ | ✔
604 |  |  | H |  |  | 19 | Y |  | ✔ | ✔ | ✔
604 |  |  | SAAB |  |  |  | Y | 2027 | ✔
604 |  |  | SAAB |  |  |  | Y | 2027 | ✔
604 |  |  | SAAB |  |  |  | Y | 2027 | ✔
603 |  |  | RHT |  |  | 19 | Y |  | ✔ | ✔ | ✔
603 |  |  | H |  |  | 19 | Y |  | ✔ | ✔ | ✔
603 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
5TH FLOOR
511 |  |  | RHT |  |  | 6 | Y |  | ✔ | ✔ | ✔
511 |  |  | H |  |  | 6 | Y |  | ✔ | ✔ | ✔
511 |  |  | SA |  |  |  |  | 2030
512 |  |  | RHT |  |  | 6 | Y |  | ✔ | ✔ | ✔
512 Hallway |  |  | RHT |  |  | 6 | Y |  | ✔ | ✔ | ✔
512 |  |  | H |  |  | 6 | Y |  | ✔ | ✔ | ✔
512 |  |  | SAAB |  |  |  | Y | 2032 | ✔
512 |  |  | SAAB |  |  |  | Y | 2031 | ✔
512 |  |  | SAAB |  |  |  | Y | 2031 | ✔
513 |  |  | RHT |  |  | 6 | Y |  | ✔ | ✔ | ✔
513 |  |  | H |  |  | 6 | Y |  | ✔ | ✔ | ✔
513 |  |  | H |  |  | 6 | Y |  | ✔ | ✔ | ✔
513 |  |  | SAAB |  |  |  | Y | 2027 | ✔
513 |  |  | SAAB |  |  |  | Y | 2027 | ✔
513 |  |  | SAAB |  |  |  | Y | 2027 | ✔
513 |  |  | SAAB |  |  |  | Y | 2029 | ✔
510 |  |  | RHT |  |  | 6 | Y |  | ✔ | ✔ | ✔
510 |  |  | H |  |  | 6 | Y |  | ✔ | ✔ | ✔
510 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
514 |  |  | RHT |  |  | 6 | Y |  | ✔ | ✔ | ✔
514 |  |  | H |  |  | 6 | Y |  | ✔ | ✔ | ✔
514 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
515 |  |  | RHT |  |  | 6 | Y |  | ✔ | ✔ | ✔
515 |  |  | H |  |  | 6 | Y |  | ✔ | ✔ | ✔
515 |  |  | SAAB |  |  |  | Y | 2033 | ✔
507 |  |  | RHT |  |  |  | Y |  | ✔ | ✔ | ✔
507 |  |  | H |  |  | 6 | Y |  | ✔ | ✔ | ✔
507 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
508 |  |  | RHT |  |  | 6 | Y |  | ✔ | ✔ | ✔
508 |  |  | H |  |  | 6 | Y |  | ✔ | ✔ | ✔
508 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
509 |  |  | RHT |  |  | 6 | Y |  | ✔ | ✔ | ✔
509 |  |  | H |  |  | 6 | Y |  | ✔ | ✔ | ✔
509 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
516 |  |  | RHT |  |  | 6 | Y |  | ✔ | ✔ | ✔
516 |  |  | H |  |  | 6 | Y |  | ✔ | ✔ | ✔
516 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
506 |  |  | RHT |  |  | 18 | Y |  | ✔ | ✔ | ✔
506 |  |  | H |  |  | 18 | Y |  | ✔ | ✔ | ✔
506 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
518 |  |  | RHT |  |  | 18 | Y |  | ✔ | ✔ | ✔
518 |  |  | H |  |  | 18 | Y |  | ✔ | ✔ | ✔
518 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
518 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
505 |  |  | RHT |  |  | 18 | Y |  | ✔ | ✔ | ✔
505 |  |  | H |  |  | 18 | Y |  | ✔ | ✔ | ✔
505 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
501 |  |  | RHT |  |  | 18 | Y |  | ✔ | ✔ | ✔
501 |  |  | H |  |  | 18 | Y |  | ✔ | ✔ | ✔
501 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
501 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
503 |  |  | RHT |  |  | 18 | Y |  | ✔ | ✔ | ✔
503 |  |  | H |  |  | 18 | Y |  | ✔ | ✔ | ✔
503 |  |  | SAA |  |  |  | Y | 2030 | ✔
504 |  |  | RHT |  |  | 18 | Y |  | ✔ | ✔ | ✔
504 |  |  | H |  |  | 18 | Y |  | ✔ | ✔ | ✔
504 Lounge |  |  | SAAB |  |  |  | Y | 2027 | ✔
504 |  |  | SAAB |  |  |  | Y | 2027 | ✔
504 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
517 |  |  | RHT |  |  | 18 | Y |  | ✔ | ✔ | ✔
517 |  |  | H |  |  | 18 | Y |  | ✔ | ✔ | ✔
517 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
502 |  |  | RHT |  |  | 18 | Y |  | ✔ | ✔ | ✔
502 |  |  | H |  |  | 18 | Y |  | ✔ | ✔ | ✔
502 |  |  | SAAB |  |  |  | Y | 2034 | ✔
4TH FLOOR
414 |  |  | RHT |  |  | 5 | Y |  | ✔ | ✔ | ✔
414 |  |  | H |  |  | 5 | Y |  | ✔ | ✔ | ✔
414 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
412 Lounge |  |  | RHT |  |  | 5 | Y |  | ✔ | ✔ | ✔
412 Hall in Suite |  |  | RHT |  |  | 5 | Y |  | ✔ | ✔ | ✔
412 |  |  | H |  |  | 5 | Y |  | ✔ | ✔ | ✔
412 Hall |  |  | SACOAB |  |  |  | Y | 2028 | ✔
412 Master |  |  | SAAB |  |  |  | Y | 2032 | ✔
412 |  |  | SAAB |  |  |  | Y | 3032 | ✔
413 |  |  | RHT |  |  | 5 | Y |  | ✔ | ✔ | ✔
413 |  |  | H |  |  | 5 | Y |  | ✔ | ✔ | ✔
413 |  |  | H |  |  | 5 | Y |  | ✔ | ✔ | ✔
413 Bedroom |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
413 Bedroom |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
413 Hall |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
413 Lounge |  |  | SAAB |  |  |  | Y | 2028 | ✔
410 |  |  | RHT |  |  | 5 | Y |  | ✔ | ✔ | ✔
410 |  |  | H |  |  | 5 | Y |  | ✔ | ✔ | ✔
410 |  |  | SAALi |  |  |  | Y | 2030 | ✔
411 |  |  | RHT |  |  | 5 | Y |  | ✔ | ✔ | ✔
411 |  |  | H |  |  | 5 | Y |  | ✔ | ✔ | ✔
411 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
416 |  |  | RHT |  |  | 5 | Y |  | ✔ | ✔ | ✔
416 |  |  | H |  |  | 5 | Y |  | ✔ | ✔ | ✔
416 |  |  | SAA |  |  |  | Y | 2034 | ✔
415 |  |  | RHT |  |  | 5 | Y |  | ✔ | ✔ | ✔
415 |  |  | H |  |  | 5 | Y |  | ✔ | ✔ | ✔
415 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
409 |  |  | RHT |  |  | 5 | Y |  | ✔ | ✔ | ✔
409 |  |  | H |  |  | 5 | Y |  | ✔ | ✔ | ✔
409 |  |  | SAAB |  |  |  | Y | 2034 | ✔
408 |  |  | RHT |  |  | 5 | Y |  | ✔ | ✔ | ✔
408 |  |  | H |  |  | 5 | Y |  | ✔ | ✔ | ✔
408 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
407 |  |  | RHT |  |  | 5 | Y |  | ✔ | ✔ | ✔
407 |  |  | H |  |  | 5 | Y |  | ✔ | ✔ | ✔
407 |  |  | SAALi | YES |  |  | Y | ✖ | ✔ |  |  |  | Failed - Low Audio
406 |  |  | RHT |  |  | 17 | Y |  | ✔ | ✔ | ✔
406 |  |  | H |  |  | 17 | Y |  | ✔ | ✔ | ✔
406 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
418 |  |  | RHT |  |  | 17 | Y |  | ✔ | ✔ | ✔
418 |  |  | H |  |  | 17 | Y |  | ✔ | ✔ | ✔
418 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
418 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
405 |  |  | RHT |  |  | 17 | Y |  | ✔ | ✔ | ✔
405 |  |  | H |  |  | 17 | Y |  | ✔ | ✔ | ✔
405 |  |  | SAAB |  |  |  | Y | 2031 | ✔
401 |  |  | RHT |  |  | 17 | Y |  | ✔ | ✔ | ✔
401 |  |  | H |  |  | 17 | Y |  | ✔ | ✔ | ✔
401 |  |  | SAAB |  |  |  | Y | 2029 | ✔
401 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
402 |  |  | RHT |  |  | 17 | Y |  | ✔ | ✔ | ✔
402 |  |  | H |  |  | 17 | Y |  | ✔ | ✔ | ✔
402 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
403 |  |  | RHT |  |  | 17 | Y |  | ✔ | ✔ | ✔
403 |  |  | H |  |  | 17 | Y |  | ✔ | ✔ | ✔
403 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
404 |  |  | RHT |  |  | 17 | Y |  | ✔ | ✔ | ✔
404 |  |  | H |  |  | 17 | Y |  | ✔ | ✔ | ✔
404 |  |  | SAAB |  |  |  | Y | 2033 | ✔
404 |  |  | SAAB |  |  |  | Y | 2034 | ✔
404 |  |  | SAAB |  |  |  | Y | 2034 | ✔
417 |  |  | RHT |  |  | 17 | Y |  | ✔ | ✔ | ✔
417 |  |  | H |  |  | 17 | Y |  | ✔ | ✔ | ✔
417 |  |  | SAAB |  |  |  | Y | 2030 | ✔
3RD FLOOR
311 |  |  | RHT |  |  | 4 | Y |  | ✔ | ✔ | ✔
311 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
311 |  |  | SAALi |  |  |  | Y | 2030 | ✔
312 |  |  | RHT |  |  | 4 | Y |  | ✔ | ✔ | ✔
312 Hallway |  |  | RHT |  |  | 4 | Y |  | ✔ | ✔ | ✔
312 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
312 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
312 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
312 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
313 |  |  | RHT |  |  | 4 | Y |  | ✔ | ✔ | ✔
313 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
313 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
313 |  |  | SAAB |  |  |  | Y | 2027 | ✔
313 |  |  | SAAB |  |  |  | Y | 2027 | ✔
313 |  |  | SAAB |  |  |  | Y | 2027 | ✔
310 |  |  | RHT |  |  | 4 | Y |  | ✔ | ✔ | ✔
310 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
310 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
314 |  |  | RHT |  |  | 4 | Y |  | ✔ | ✔ | ✔
314 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
314 |  |  | SAAB |  |  |  | Y | 2031 | ✔
315 |  |  | RHT |  |  | 4 | Y |  | ✔ | ✔ | ✔
315 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
315 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
316 |  |  | RHT |  |  | 4 | Y |  | ✔ | ✔ | ✔
316 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
316 |  |  | SAAB |  |  |  | Y | 2029 | ✔
308 |  |  | RHT |  |  | 4 | Y |  | ✔ | ✔ | ✔
308 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
308 |  |  | SAAB |  |  |  | Y | 2034 | ✔
307 |  |  | RHT |  |  | 4 | Y |  | ✔ | ✔ | ✔
307 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
307 |  |  | SAAB |  |  |  | Y | 2034 | ✔
309 |  |  | RHT |  |  | 4 | Y |  | ✔ | ✔ | ✔
309 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
309 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
317 |  |  | RHT |  |  | 16 | Y |  | ✔ | ✔ | ✔
317 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
317 |  |  | SAAB |  |  |  | Y | 2034 | ✔
318 |  |  | RHT |  |  | 16 | Y |  | ✔ | ✔ | ✔
318 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
318 |  |  | SAAB |  |  |  | Y | 2033 | ✔
318 |  |  | SAAB |  |  |  | Y | 2034 | ✔
306 |  |  | RHT |  |  | 16 | Y |  | ✔ | ✔ | ✔
306 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
306 |  |  | SAAB |  |  |  | Y | 2029 | ✔
305 |  |  | RHT |  |  | 16 | Y |  | ✔ | ✔ | ✔
305 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
305 |  |  | SAAB |  |  |  | Y | 2033 | ✔
301 |  |  | RHT |  |  | 16 | Y |  | ✔ | ✔ | ✔
301 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
301 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
301 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
302 |  |  | RHT |  |  | 16 | Y |  | ✔ | ✔ | ✔
302 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
302 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
303 |  |  | RHT |  |  | 16 | Y |  | ✔ | ✔ | ✔
303 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
303 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
304 |  |  | RHT |  |  | 16 | Y |  | ✔ | ✔ | ✔
304 |  |  | H |  |  | 4 | Y |  | ✔ | ✔ | ✔
304 |  |  | SAAB |  |  |  | Y | 2028 | ✔
304 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
304 Master Bedroom |  |  | SAA |  |  |  | Y | 2026 | ✔
2ND FLOOR
212 |  |  | RHT |  |  | 3 | Y |  | ✔ | ✔ | ✔
212 Hallway |  |  | RHT |  |  | 3 | Y |  | ✔ | ✔ | ✔
212 |  |  | H |  |  | 3 | Y |  | ✔ | ✔ | ✔
212 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
212 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
212 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
213 |  |  | RHT |  |  | 3 | Y |  | ✔ | ✔ | ✔
213 |  |  | H |  |  | 3 | Y |  | ✔ | ✔ | ✔
213 |  |  | SAAB |  |  |  | Y | 2027 | ✔
213 |  |  | SAAB |  |  |  | Y | 2027 | ✔
213 |  |  | SAAB |  |  |  | Y | 2027 | ✔
213 |  |  | SAAB |  |  |  | Y | 2027 | ✔
210 |  |  | RHT |  |  | 3 | Y |  | ✔ | ✔ | ✔
210 |  |  | H |  |  | 3 | Y |  | ✔ | ✔ | ✔
210 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
214 |  |  | RHT |  |  | 3 | Y |  | ✔ | ✔ | ✔
214 |  |  | H |  |  | 3 | Y |  | ✔ | ✔ | ✔
214 |  |  | SAAB |  |  |  | Y | 2036 | ✔
215 |  |  | RHT |  |  | 3 | Y |  | ✔ | ✔ | ✔
215 |  |  | H |  |  | 3 | Y |  | ✔ | ✔ | ✔
215 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
209 |  |  | RHT |  |  | 3 | Y |  | ✔ | ✔ | ✔
209 |  |  | H |  |  | 3 | Y |  | ✔ | ✔ | ✔
209 |  |  | SAALi |  |  |  | Y | 2030 | ✔
216 |  |  | RHT |  |  | 3 | Y |  | ✔ | ✔ | ✔
216 |  |  | H |  |  | 3 | Y |  | ✔ | ✔ | ✔
216 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
208 |  |  | RHT |  |  | 3 | Y |  | ✔ | ✔ | ✔
208 |  |  | H |  |  | 3 | Y |  | ✔ | ✔ | ✔
208 |  |  | SAALi |  |  |  | Y | 2030 | ✔
207 |  |  | RHT |  |  | 3 | Y |  | ✔ | ✔ | ✔
207 |  |  | H |  |  | 3 | Y |  | ✔ | ✔ | ✔
207 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
211 |  |  | RHT |  |  | 3 | Y |  | ✔ | ✔ | ✔
211 |  |  | H |  |  | 3 | Y |  | ✔ | ✔ | ✔
211 |  |  | SAAB |  |  |  | Y | 2027 | ✔
217 |  |  | RHT |  |  | 15 | Y |  | ✔ | ✔ | ✔
217 |  |  | H |  |  | 15 | Y |  | ✔ | ✔ | ✔
217 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
218 |  |  | RHT |  |  | 15 | Y |  | ✔ | ✔ | ✔
218 |  |  | H |  |  | 15 | Y |  | ✔ | ✔ | ✔
218 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
218 |  |  | SAAB |  |  |  | Y | 2030 | ✔
205 |  |  | RHT |  |  | 15 | Y |  | ✔ | ✔ | ✔
205 |  |  | H |  |  | 15 | Y |  | ✔ | ✔ | ✔
205 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
201 |  |  | RHT |  |  | 15 | Y |  | ✔ | ✔ | ✔
201 |  |  | H |  |  | 15 | Y |  | ✔ | ✔ | ✔
201 |  |  | SAAB |  |  |  | Y | 2027 | ✔
201 |  |  | SAAB |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
202 |  |  | RHT |  |  | 15 | Y |  | ✔ | ✔ | ✔
202 |  |  | H |  |  | 15 | Y |  | ✔ | ✔ | ✔
202 |  |  | SAALi |  |  |  | Y | 2030 | ✔
204 |  |  | RHT |  |  | 15 | Y |  | ✔ | ✔ | ✔
204 |  |  | H |  |  | 15 | Y |  | ✔ | ✔ | ✔
204 |  |  | SAAB |  |  |  | Y | 2026 | ✔
204 |  |  | SAAB |  |  |  | Y | 2032 | ✔
204 |  |  | SAAB |  |  |  | Y | 2031 | ✔
203 |  |  | RHT |  |  | 15 | Y |  | ✔ | ✔ | ✔
203 |  |  | H |  |  | 15 | Y |  | ✔ | ✔ | ✔
203 |  |  | SAAB |  |  |  | Y | 2028 | ✔
206 |  |  | RHT |  |  | 15 | Y |  | ✔ | ✔ | ✔
206 |  |  | H |  |  | 15 | Y |  | ✔ | ✔ | ✔
206 |  |  | SAA |  |  |  | Y | OLD | ✔ |  |  |  | Recommend Replacement
COMMON AREAS - 8TH FLOOR
Elevator Machine Room |  |  | S |  |  | 12 | Y |  | ✔ | ✔ | ✔ |  | Homes to 1st Floor
Elevator Machine Room |  |  | RELAY | [9 empty] | Elevator Homing by Shaft and Machine Room
Elevator Machine Room |  |  | RELAY | [9 empty] | Elevator Alternate Homing
Elevator Machine Room |  |  | RELAY | [9 empty] | Elevator Homing
Elevator Top of Shaft (Elevator#2) |  |  | S |  |  | 13 | Y |  | ✔ | ✔ | ✔ |  | SIGA-HRS / No Access May 2025
Elevator Pit (Elevator#2) |  |  | RHT |  |  | 13 | Y |  | ✔ | ✔ | ✔ |  | SIGA-PS / No Access May 2025
East Closet | 13 |  | RHT |  |  | 9 | Y |  | ✔ | ✔ | ✔
East Electrical Closet | 14 |  | RHT |  |  | 9 | Y |  | ✔ | ✔ | ✔ |  | ROOF ACCESS
Hallway by 810 | 16 |  | S |  |  | 9 | Y |  | ✔ | ✔ | ✔
Hallway by 814 | 10 |  | S |  |  | 9 | Y |  | ✔ | ✔ | ✔
Hallway by 809 (804) | 15 |  | S |  |  | 9 | Y |  | ✔ | ✔ | ✔
Hallway by 808 | 11 |  | S |  |  | 9 | Y |  | ✔ | ✔ | ✔
Hallway by 813 | 12 |  | S |  |  | 9 | Y |  | ✔ | ✔ | ✔
Exit at Smoke Doors | 9 |  | M |  |  | 9 | Y |  | ✔ | ✔ | ✔
East Stair Exit | 18 |  | EOL |  |  |  | Y
East Stair Exit | 17 |  | M |  |  | 9 | Y |  | ✔ | ✔ | ✔ |  | SIGA 270; EOL above
Hallway by 802 | 3 |  | S |  |  | 21 | Y |  | ✔ | ✔ | ✔
Closet by 804 | 6 |  | S |  |  | 21 | Y |  | ✔ | ✔ | ✔
Hallway by Elevator | 4 |  | S |  |  | 21 | Y |  | ✔ | ✔ | ✔
Hallway by West Closet | 5 |  | S |  |  | 21 | Y |  | ✔ | ✔ | ✔
Hallway by 815 | 7 |  | S |  |  | 21 | Y |  | ✔ | ✔ | ✔
West Stair Exit by 802 | 2 |  | M |  |  | 21 | Y |  | ✔ | ✔ | ✔
Exit at Smoke Doors West | 8 |  | M |  |  | 21 | Y |  | ✔ | ✔ | ✔
Top of Stairs East | 19 |  | S |  |  | 10 | Y |  | ✔ | ✔ | ✔
Top of Stairs West | 1 |  | S |  |  | 11 | Y |  | ✔ | ✔ | ✔
West Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
West Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
8th Floor Centre |  |  | DH |  |  |  | Y |  | ✔ | ✔ | ✔ |  | Closes on Alarm
West Closet by Elevator |  |  | RELAY | [9 empty] | 8th Floor Door Holder
West Closet by Elevator |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 8 Hallway
West Closet by Elevator |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 8 Suites
West Closet by Elevator |  |  | EOL |  |  |  | Y
COMMON AREAS - 7TH FLOOR
East Electrical Closet | 3 |  | S |  |  | 8 | Y |  | ✔ | ✔ | ✔
Hallway by 715 | 5 |  | S |  |  | 8 | Y |  | ✔ | ✔ | ✔
Hallway by 713 | 4 |  | S |  |  | 8 | Y |  | ✔ | ✔ | ✔
Hallway by 707 | 6 |  | S |  |  | 8 | Y |  | ✔ | ✔ | ✔
Hallway by 712 | 2 |  | S |  |  | 8 | Y |  | ✔ | ✔ | ✔
Exit at Smoke Door by 707 | 7 |  | M |  |  | 8 | Y |  | ✔ | ✔ | ✔
East Stair Exit | 1 |  | M |  |  | 8 | Y |  | ✔ | ✔ | ✔
Hallway by Elevator | 11 |  | S |  |  | 20 | Y |  | ✔ | ✔ | ✔
Hallway by 703 | 14 |  | S |  |  | 20 | Y |  | ✔ | ✔ | ✔
Closet by Stairs (Utility Room by 704) | 16 |  | S |  |  | 20 | Y |  | ✔ | ✔ | ✔
Closet by 701 | 13 |  | S |  |  | 20 | Y |  | ✔ | ✔ | ✔
Hallway by 701 | 12 |  | S |  |  | 20 | Y |  | ✔ | ✔ | ✔
Hallway by 717 | 9 |  | S |  |  | 20 | Y |  | ✔ | ✔ | ✔
West Stair Exit by 704 | 17 |  | M |  |  | 20 | Y |  | ✔ | ✔ | ✔
Exit at Smoke Doors by 717 | 8 |  | M |  |  | 20 | Y |  | ✔ | ✔ | ✔
West Meter Closet by 706 | 10 |  | RHT |  |  | 20 | Y |  | ✔ | ✔ | ✔
West Shaft Closet by 703 | 15 |  | S |  |  | 20 | Y |  | ✔ | ✔ | ✔
West Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
7th Floor Centre |  |  | DH |  |  |  | Y |  | ✔ | ✔ | ✔ |  | Closes on Alarm
Closet by 718 |  |  | RELAY | [9 empty] | 7th Floor Door Holder
Closet by 718 |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 7 Hallway
Closet by 718 |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 7 Suites
COMMON AREAS - 6TH FLOOR
Electrical Closet by 611 | 17 |  | S |  |  | 7 | Y |  | ✔ | ✔ | ✔
Hallway by 612 | 18 |  | S |  |  | 7 | Y |  | ✔ | ✔ | ✔
Hallway by 613 | 16 |  | S |  |  | 7 | Y |  | ✔ | ✔ | ✔
Hallway by 615 | 14 |  | S |  |  | 7 | Y |  | ✔ | ✔ | ✔
Hallway by 607 | 13 |  | S |  |  | 7 | Y |  | ✔ | ✔ | ✔
East Stair Exit by 612 | 19 |  | M |  |  | 7 | Y |  | ✔ | ✔ | ✔
At Smoke Door by 607 | 12 |  | M |  |  | 7 | Y |  | ✔ | ✔ | ✔
East Storage by 613 | 15 |  | RHT |  |  | 7 | Y |  | ✔ | ✔ | ✔ |  | No Access April 2023 - May 2025
Hallway by 617 | 10 |  | S |  |  | 19 | Y |  | ✔ | ✔ | ✔
Hallway by Elevator | 8 |  | S |  |  | 19 | Y |  | ✔ | ✔ | ✔
Hallway by 601 | 6 |  | S |  |  | 19 | Y |  | ✔ | ✔ | ✔
Utility Closet by 601 | 7 |  | S |  |  | 19 | Y |  | ✔ | ✔ | ✔
Storage 602 | 4 |  | S |  |  | 19 | Y |  | ✔ | ✔ | ✔
Utility Closet by 602 | 5 |  | S |  |  | 19 | Y |  | ✔ | ✔ | ✔
Hall by 603 | 3 |  | S |  |  | 19 | Y |  | ✔ | ✔ | ✔
Exit at Smoke Doors by 617 | 11 |  | M |  |  | 19 | Y |  | ✔ | ✔ | ✔
West Stair Exit by 604 | 2 |  | M |  |  | 19 | Y |  | ✔ | ✔ | ✔
West Meter Closet | 9 |  | RHT |  |  | 19 | Y |  | ✔ | ✔ | ✔
West Stairs Level 6 | 1 |  | S |  |  | 11 | Y |  | ✔ | ✔ | ✔
East Stairs Level 6 | 20 |  | S |  |  | 10 | Y |  | ✔ | ✔ | ✔
West Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
6th Floor Centre |  |  | DH |  |  |  | Y |  | ✔ | ✔ | ✔ |  | Closes on Alarm
West Closet by Elevator |  |  | RELAY | [9 empty] | 6th Floor Door Holder
West Closet by Elevator |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 6 Hallway
West Closet by Elevator |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 6 Suite
COMMON AREAS - 5TH FLOOR
East Electrical Closet by 511 | 3 |  | S |  |  | 6 | Y |  | ✔ | ✔ | ✔
Hallway by 512 | 2 |  | S |  |  | 6 | Y |  | ✔ | ✔ | ✔
Hallway by 513 | 4 |  | S |  |  | 6 | Y |  | ✔ | ✔ | ✔
Hall at Smoke Door by 507 | 6 |  | S |  |  | 6 | Y |  | ✔ | ✔ | ✔
At Smoke Door by 507 | 7 |  | M |  |  | 6 | Y |  | ✔ | ✔ | ✔
East Stair Exit by 515 | 1 |  | M |  |  | 6 | Y |  | ✔ | ✔ | ✔
Hallway by 515 | 5 |  | S |  |  | 6 | Y |  | ✔ | ✔ | ✔
Hallway by Elevator | 11 |  | S |  |  | 18 | Y |  | ✔ | ✔ | ✔
Hallway by 501 | 12 |  | S |  |  | 18 | Y |  | ✔ | ✔ | ✔
Closet by 501 | 13 |  | S |  |  | 18 | Y |  | ✔ | ✔ | ✔
Closet by Stairs (503) | 15 |  | S |  |  | 18 | Y |  | ✔ | ✔ | ✔
Hallway by 503 | 14 |  | S |  |  | 18 | Y |  | ✔ | ✔ | ✔
Utility Room (502) | 16 |  | S |  |  | 18 | Y |  | ✔ | ✔ | ✔
Hall at Smoke Door by 517 | 9 |  | S |  |  | 18 | Y |  | ✔ | ✔ | ✔
At Smoke Door by 517 | 8 |  | M |  |  | 18 | Y |  | ✔ | ✔ | ✔
West Stair Exit | 17 |  | M |  |  | 18 | Y |  | ✔ | ✔ | ✔
West Meter Closet by 518 | 10 |  | RHT |  |  | 18 | Y |  | ✔ | ✔ | ✔
West Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
5th Floor Centre |  |  | DH |  |  |  | Y |  | ✔ | ✔ | ✔ |  | Closes on Alarm
West Closet by Elevator |  |  | RELAY | [9 empty] | 5th Floor Door Holder
West Closet by Elevator |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 5 Hallway
West Closet by Elevator |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 5 Suites
COMMON AREAS - 4TH FLOOR
East Electrical Closet by 411 | 17 |  | S |  |  | 5 | Y |  | ✔ | ✔ | ✔
Hallway by 413 | 16 |  | S |  |  | 5 | Y |  | ✔ | ✔ | ✔
Hallway by 415 (409) | 14 |  | S |  |  | 5 | Y |  | ✔ | ✔ | ✔
Hallway by 407 | 13 |  | S |  |  | 5 | Y |  | ✔ | ✔ | ✔
Hallway by 412 | 18 |  | S |  |  | 5 | Y |  | ✔ | ✔ | ✔
East Stair Exit by 412 | 19 |  | M |  |  | 5 | Y |  | ✔ | ✔ | ✔
At Smoke Door by 407 | 12 |  | M |  |  | 5 | Y |  | ✔ | ✔ | ✔
East Storage by 413 | 15 |  | RHT |  |  | 5 | Y |  | ✔ | ✔ | ✔
Hallway by 402 | 6 |  | S |  |  | 17 | Y |  | ✔ | ✔ | ✔
Closet by 401 | 7 |  | S |  |  | 17 | Y |  | ✔ | ✔ | ✔
West Meter Closet by 418 | 15 |  | RHT |  |  |  | Y |  | ✔ | ✔ | ✔ |  | Unable to test May 2025 - Heat Gun required (solo tester will not work)
West Utility Closet by 404 | 4 |  | S |  |  | 17 | Y |  | ✔ | ✔ | ✔
Hallway by 403 | 3 |  | S |  |  | 17 | Y |  | ✔ | ✔ | ✔
Hallway by 417 | 10 |  | S |  |  | 17 | Y |  | ✔ | ✔ | ✔
Hallway by Elevator | 8 |  | S |  |  | 17 | Y |  | ✔ | ✔ | ✔
Storage by 402 | 5 |  | S |  |  | 17 | Y |  | ✔ | ✔ | ✔
At Smoke Door by 417 | 11 |  | M |  |  | 17 | Y |  | ✔ | ✔ | ✔
West Stair Exit by 404 | 2 |  | M |  |  | 17 | Y |  | ✔ | ✔ | ✔
East Stairs Level 4 | 20 |  | S |  |  | 10 | Y |  | ✔ | ✔ | ✔
West Stairs Level 4 | 1 |  | S |  |  | 11 | Y |  | ✔ | ✔ | ✔
West Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
4th Floor Centre |  |  | DH |  |  |  | Y |  | ✔ | ✔ | ✔ |  | Closes on Alarm
West Closet by Elevator |  |  | RELAY | [9 empty] | 4th Floor Door Holder
West Closet by Elevator |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 4 Hallway
West Closet by Elevator |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 4 Suites
COMMON AREAS - 3RD FLOOR
East Electrical Closet by 311 | 3 |  | S |  |  | 4 | Y |  | ✔ | ✔ | ✔
Hallway by 313 | 4 |  | S |  |  | 4 | Y |  | ✔ | ✔ | ✔
Hallway by 315 ( 309) | 5 |  | S |  |  | 4 | Y |  | ✔ | ✔ | ✔
Hallway by 312 | 2 |  | S |  |  | 4 | Y |  | ✔ | ✔ | ✔
Hallway by 307 | 6 |  | S |  |  | 4 | Y |  | ✔ | ✔ | ✔
East Stair Exit by 312 | 1 |  | M |  |  | 4 | Y |  | ✔ | ✔ | ✔
At Smoke Door by 307 | 7 |  | M |  |  | 4 | Y |  | ✔ | ✔ | ✔
Hall by Elevator | 11 |  | S |  |  | 16 | Y |  | ✔ | ✔ | ✔
Hallway by 301 | 12 |  | S |  |  | 16 | Y |  | ✔ | ✔ | ✔
Closet by 301 | 13 |  | S |  |  | 16 | Y |  | ✔ | ✔ | ✔
Storage by 302 | 15 |  | S |  |  | 16 | Y |  | ✔ | ✔ | ✔
Hallway by 303 | 14 |  | S |  |  | 16 | Y |  | ✔ | ✔ | ✔
Westend Closet (303) | 16 |  | S |  |  | 16 | Y |  | ✔ | ✔ | ✔
Hallway by 317 | 9 |  | S |  |  | 16 | Y |  | ✔ | ✔ | ✔
At Smoke Door by 317 | 8 |  | M |  |  | 16 | Y |  | ✔ | ✔ | ✔
West Stair Exit by 304 | 17 |  | M |  |  | 16 | Y |  | ✔ | ✔ | ✔
West Meter Closet (301) | 10 |  | RHT |  |  | 16 | Y |  | ✔ | ✔ | ✔
West Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
3th Floor Centre |  |  | DH |  |  |  | Y |  | ✔ | ✔ | ✔ |  | Closes on Alarm
West Closet by Elevator |  |  | RELAY | [9 empty] | 3rd Floor Door Holder
West Closet by Elevator |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 3 Hallway
West Closet by Elevator |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 3 Suites
COMMON AREAS - 2ND FLOOR
East Electrical Closet | 17 |  | S |  |  | 3 | Y |  | ✔ | ✔ | ✔
Hallway by 211 | 18 |  | S |  |  | 3 | Y |  | ✔ | ✔ | ✔
Hallway by 213 | 16 |  | S |  |  | 3 | Y |  | ✔ | ✔ | ✔
Hallway by 215 (209) | 14 |  | S |  |  | 3 | Y |  | ✔ | ✔ | ✔
Hallway by 207 | 13 |  | S |  |  | 3 | Y |  | ✔ | ✔ | ✔
East Storage by 213 | 15 |  | RHT |  |  | 3 | Y |  | ✔ | ✔ | ✔
At Smoke Door by 207 | 12 |  | M |  |  | 3 | Y |  | ✔ | ✔ | ✔
East Stair Exit | 19 |  | M |  |  | 3 | Y |  | ✔ | ✔ | ✔
Hallway by Elevator | 8 |  | S |  |  | 15 | Y |  | ✔ | ✔ | ✔ |  | Replaced July 2025
Hallway by 217 | 10 |  | S |  |  | 15 | Y |  | ✔ | ✔ | ✔
Hallway by 201 (202) | 6 |  | S |  |  | 15 | Y |  | ✔ | ✔ | ✔
Closet by 201 | 7 |  | S |  |  | 15 | Y |  | ✔ | ✔ | ✔
Closet by 202 | 4 |  | S |  |  | 15 | Y |  | ✔ | ✔ | ✔
West Hall Closet by 204 | 5 |  | RHT |  |  | 15 | Y |  | ✔ | ✔ | ✔
West Stair #1 by 204 | 1 |  | S |  |  | 15 | Y |  | ✔ | ✔ | ✔
Hallway by 203 | 3 |  | S |  |  | 15 | Y |  | ✔ | ✔ | ✔
West at Smoke Door by 217 | 11 |  | M |  |  | 15 | Y |  | ✔ | ✔ | ✔
West Stair Exit by 204 | 2 |  | M |  |  | 15 | Y |  | ✔ | ✔ | ✔
West Meter Closet | 9 |  | RHT |  |  | 15 | Y |  | ✔ | ✔ | ✔ |  | Unable to test May 2025 - Heat Gun required (solo tester will not work)
East Stairs Level 2 | 20 |  | S |  |  | 10 | Y |  | ✔ | ✔ | ✔
West Stairs Level 2 |  |  | S |  |  | 11 | Y |  | ✔ | ✔ | ✔ |  | Unable to locate - May 2025
West Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Hall |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
2nd Floor Centre |  |  | DH |  |  |  | Y |  | ✔ | ✔ | ✔ |  | Closes on Alarm
West Closet by Elevator |  |  | RELAY | [9 empty] | 2nd Floor Door Holder
West Closet by Elevator |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 2 Hallway
West Closet by Elevator |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 2 Suites
MAIN FLOOR
Main Entrance | 1 |  | M |  |  | 2 | Y |  | ✔ | ✔ | ✔
Main Entrance Lobby (West) | 2 |  | S |  |  | 2 | Y |  | ✔ | ✔ | ✔ |  | Replaced by Troy Life & Safety July 2024
Centre West Lobby Smoke | 3 |  | S |  |  | 2 | Y |  | ✔ | ✔ | ✔
Lounge East Exit | 4 |  | M |  |  | 2 | Y |  | ✔ | ✔ | ✔
North Stair Exit | 5 |  | M |  |  | 2 | Y |  | ✔ | ✔ | ✔
Elevator Hallway | 6 |  | S |  |  | 2 | Y |  | ✔ | ✔ | ✔
East Hallway Exit | 7 |  | M |  |  | 2 | Y |  | ✔ | ✔ | ✔
West Storage #2 Exit (Exterior) | 8 |  | M |  |  | 2 | Y |  | ✔ | ✔ | ✔
West Storage #1 Exit (Exterior) | 9 |  | M |  |  | 2 | Y |  | ✔ | ✔ | ✔
Bulb Storage Room East (Exterior) | 10 |  | S |  |  | 2 | Y |  | ✔ | ✔ | ✔
Center Corridor |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
Common Lounge |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
Entry Lobby |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
Storage #2 |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
Level 1 Hallway |  |  | ISO-A |  |  |  | Y | [5 empty] | Level 1
East Hallway Fan Control |  |  | RELAY | [9 empty] | Turns on with alarm
West Hallway Fan Control |  |  | RELAY | [9 empty] | Turns on with alarm
Level 1 Commercial Unit |  |  | ISO-A |  |  |  | Y
Lounge |  |  | APT | [9 empty] | Purpose unknown
COMMERCIAL
665 Douglas SW Exit |  |  | M |  |  | 22 | Y |  | ✔ | ✔ | ✔
665 Douglas Rear Exit |  |  | M |  |  | 22 | Y |  | ✔ | ✔ | ✔
665 Back Hall |  |  | H/V |  |  |  | Y |  | ✔ | ✔ | ✔
665 Lab1 |  |  | H/V |  |  |  | Y |  | ✔ | ✔ | ✔
665 Lab 2 |  |  | H/V |  |  |  | Y |  | ✔ | ✔ | ✔
665 Office Area |  |  | H/V |  |  |  | Y |  | ✔ | ✔ | ✔
BASEMENT
Workshop |  |  | RHT |  |  | 1 | Y |  | ✔ | ✔ | ✔
Communications Room |  |  | RHT |  |  | 1 | Y |  | ✔ | ✔ | ✔
North Exit by Stairs |  |  | M |  |  | 1 | Y |  | ✔ | ✔ | ✔
Center Corridor |  |  | S |  |  | 1 | Y |  | ✔ | ✔ | ✔
Parkade Entry |  |  | S |  |  | 1 | Y |  | ✔ | ✔ | ✔
Center Elevator Hallway |  |  | S |  |  | 1 | Y |  | ✔ | ✔ | ✔
West Corridor by Gym |  |  | S |  |  | 1 | Y |  | ✔ | ✔ | ✔
Boiler Room North |  |  | RHT |  |  | 1 | Y |  | ✔ | ✔ | ✔
Boiler Room Fire Pump |  |  | RELAY |  |  | 29
Telephone/Data Room |  |  | S |  |  | 1 | Y |  | ✔ | ✔ | ✔ |  | Access through Boiler Room
Laundry Room |  |  | RHT |  |  | 1 | Y |  | ✔ | ✔ | ✔
Storage #3 |  |  | S |  |  | 1 | Y |  | ✔ | ✔ | ✔ |  | Replaced by Troy Life & Safety September 2024
West Gym Exit |  |  | M |  |  | 1 | Y |  | ✔ | ✔ | ✔
West Parkade Exit Hallway West |  |  | RHT |  |  | 1 | Y |  | ✔ | ✔ | ✔ |  | SIGA-HRS - solo tester
West Parkade Exit Hallway East |  |  | RHT |  |  | 1 | Y |  | ✔ | ✔ | ✔ |  | SIGA-HRS - solo tester
West Parkade Exit Hallway West |  |  | M |  |  | 1 | Y |  | ✔ | ✔ | ✔
Recycling (Garbage) Room |  |  | RHT |  |  | 1 | Y |  | ✔ | ✔ | ✔
Parkade E. Storage (Bicycle) Utility Room 4 |  |  | S |  |  | 1 | Y |  | ✔ | ✔ | ✔
East Paint Storage#1 Utility Room 4 |  |  | S |  |  | 1 | Y |  | ✔ | ✔ | ✔ |  | Through East Storage Room
Paint Room Storage#2 Utility Room 4 |  |  | RHT |  |  | 1 | Y |  | ✔ | ✔ | ✔ |  | Through East Storage Room
Bike Room Exit |  |  | M |  |  | 1 | Y |  | ✔ | ✔ | ✔
Bike Room SW |  |  | S |  |  | 1 | Y |  | ✔ | ✔ | ✔
Bike Room West |  |  | S |  |  | 1 | Y |  | ✔ | ✔ | ✔
Bike Room Centre |  |  | RHT |  |  | 1 | Y |  | ✔ | ✔ | ✔
Bike Room East |  |  | S |  |  | 1 | Y |  | ✔ | ✔ | ✔
Electrical Room |  |  | RHT |  |  | 1 | Y |  | ✔ | ✔ | ✔
Generator Room |  |  | S |  |  | 1 | Y |  | ✔ | ✔ | ✔ |  | Padlock broken - Pull Padlock to open (2025)
West Bike Storage |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
Recycling Room |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
West Gym |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
East Storage(outside Gate) |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
Center Corridor |  |  | H |  |  |  | Y |  | ✔ | ✔ | ✔
Basement |  |  | ISO-A |  |  | 1 | Y | [5 empty] | Basement Level
FACP
Above FACP |  |  | ISO-D |  |  |  | Y | [5 empty] | Basement
Above FACP |  |  | ISO-D |  |  |  | Y | [5 empty] | Level-1
Above FACP |  |  | ISO-D |  |  |  | Y | [5 empty] | Level-2
Above FACP |  |  | ISO-D |  |  |  | Y | [5 empty] | Level-3
Above FACP |  |  | ISO-D |  |  |  | Y | [5 empty] | Level-4
Above FACP |  |  | ISO-D |  |  |  | Y | [5 empty] | Level-5
Above FACP |  |  | ISO-D |  |  |  | Y | [5 empty] | Level-6
Above FACP |  |  | ISO-D |  |  |  | Y | [5 empty] | Level-7
Above FACP |  |  | ISO-D |  |  |  | Y | [5 empty] | Level-8
Above FACP |  |  | ISO-D |  |  |  | Y | [5 empty] | Level-9
Note on A13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Text will wrap
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Text will wrap
Note on F13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Formatted as text so numbers stay as you enter them. Especially helpful for addresses
Note on G13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Formatted as text so numbers stay as you enter them. Especially helpful for addresses
Note on I13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Formatted as text so numbers stay as you enter them. Especially helpful for addresses
Note on N13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Text will wrap

## 23.3 CircuitFaultTolerance
Section 33.3 Subsequent Alarm (Alarm Resound) Control Panel Test Sheet
NOTE 1 : Refer to 8.3.1(o)
Initial fire alarm input zone test location |  | Field device label |  | subsequent alarm activation test (following alarm signal silence) |  |  | Field device label | Alarm signals remain silent |  | Note: If signals re-activated following signal silence - in result of fire alarm device
Identify NBC zone designation where initial fire alarm condition was activated |  | Identify fire alarm device used to initiate fire alarm signals activation |  | Identify NBC zone designation where subsequent fire alarm device was activated following alarm signal silence |  |  | Identify subsequent fire alarm device activated in same NBC zone following signal silence | Yes | No | Record system deficiency in Section 28.2, Deficiencies
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
NOTE: Where devices are added to an existing system which was designed and approved with a different sequence of re-sounding operation and the operation of the new devices conform to the original sequence of operation, this may not be considered a deficiency. If system modification is executed in accordance with Section 27, System Modifications, a recommendation can be made to improve an existing system in the appropriate section.
23.3 Circuit Fault Tolerance Test Sheet
NOTE 1 : Refer to Section 12 and 13
NOTE 2: Refer to Annex A, A3.86 for an explanation regarding the National Building Code (NBC) Fire Alarm (FA) Zone.
Circuit Fault Tolerance Test Sheet
| Building name : | The Q Apartments |  |  | Date (M/D/Y) : | May 21 - 23, 2025 |  | Page | ? | of | ?
Circuit fault test location |  | Type of fault (Record response time or indicate N/A) |  |  | Isolation results |  |  | Non-faulted circuit location
Identify Device Location where circuit fault was introduced and description of affected NBC Fire Alarm zone or area |  | Short | Open | Ground | Identify NBC Fire Alarm Zone or area Location where devices failed due to fault condition |  |  | Identify Individual Device tested for operation located in Non-Faulted NBC Fire Alarm zone or area |  |  | Pass or Fail