## APPENDIX C-C1 FAS VER template (hidden)
APPENDIX C (INFORMATIVE) - FIRE ALARM SYSTEM VERIFICATION REPORTS
(Reference: Subsection 4.1, Clauses 4.1.7, 4.2.1, and 4.2.2)
C1. FIRE ALARM SYSTEM VERIFICATION REPORT
(Reference: Clauses 4.1.6, 4.2.2)
Building Name: |  |  |  | Date:
Address:
System Manufacturer/ Model Number:
[5 empty] | YES | NO | N/A
A | System provides single-stage operation. | [5 empty] | -
B | System provides two-stage operation. | [5 empty] | -
C | The entire fire alarm system has been verified in accordance with CAN/ULC-S537, Standard for Verification of Fire Alarm Systems. | [5 empty] | -
D | This is a partial verification for a partial occupancy. | [5 empty] | -
E | This is a partial verification for a fire alarm system that has been replaced in stages. | [5 empty] | -
F | This is a verification of a portion of an existing fire alarm system verified in accordance with Section 7, System Modifications. | [5 empty] | -
G | Installed in accordance with the design and CAN/ULC-S524, Standard for Installation of Fire Alarm Systems. | [5 empty] | -
H | The fire alarm system documentation is on site and includes a description of the system. | [5 empty] | -
I | The fire alarm system is fully functional.
J | The fire alarm system is connected to a fire signal receiving centre. If connected, indicate the fire signal receiving centre. | [5 empty] | -
K | Comments | Please note a copy of the verification report must be added to the fire safety plan binder.
L | A copy of this report will be given to the following, who is the owner or owner's representative for this building: | [5 empty] | -
This is to certify that the information contained in this Fire Alarm System Verification Report is correct and complete.
Printed Name of Primary or Supervising Technician Conducting the Verification |  |  | Company |  | Telephone
Signature of Primary or Supervising Technician Conducting the Verification |  |  | Identification Number of Primary or Supervising Technician Conducting the Verification
Printed Name of Technician Conducting the Verification |  |  | Company |  | Telephone
Signature of Technician Conducting the Verification |  |  | Identification Number of Technician Conducting the Verification
Printed Name of Designer |  |  | Company |  | Telephone
Signature of Designer

## ULC Coverpage (hidden)
100E Burnside Rd West, Victoria, BC, V9A 1B8
Phone: (250) 475-6077
projects@cantec.ca
www.cantec.ca
Fire Alarm System Verification Report
Prepared in compliance with the 2024 BC Building Code, adopted March 8th, 2024
|  | Prepared for: | 0
|  | Building Address: | 1234
|  | Building Name: | TEST
|  | Date: | 2025-01-12
Proud to have been serving Vancouver Island for over 50 Years.
Applicable Codes & Standards References:
2024 BC Building Code Table 1.3.1.2 & Sentence 1.3.1.2.(1)
2024 BC Building Code Sentence 3.2.4.5.(2) "Fire alarm systems shall be verified in conformance with CAN/ULC-S537-19"
Part 28 "Fire Alarm System Verification Report" of CAN/ULC-S537-19 the "Standard for Verification of Fire Alarm Systems
Please Note: CAN/ULC-S537-19 requires that this "documentation be readily available to the inspection authority, retained on site in a single location, and be revised and maintained throughout the life of the fire alarm system" It is recommended to keep this report within the Fire Safety Plan Box or near the control unit.

## 32.5 Response Times (hidden)
Section 32.5 Required System Response Times
NOTE 1 : Refer to 5.4, 8.4.1, 8.5.1 and 14.1(d).
NOTE 2 : Complete section for each control unit or transponder.
Control unit or transponder location:
Control unit or transponder identification:
A | Audible signal devices and visible signal devices within the same manually initiated fire alarm zone operated within 5 s. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Audible signal devices and visible signal devices operated within 10 s, and |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
| Subsequent input operated within 10 s. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Remote connection operated within 10 s. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | Releasing device start of sequence operated within 10 s. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Required annunciation operated within 10 s, and |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
| Subsequent input operation within 10 s. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Required central alarm and control facility operated within 10 s, and |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
| Subsequent input operation within 10 s. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Ancillary circuits operated within 10 s, and |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
| Subsequent input operation within 30 s |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
NOTE: Refer to Table 6.1 for required system response times.
Table 6.1 Required System Response Times
Output |  | Maximum response times without circuit fault condition |  | Maximum response times with circuit fault condition
|  | First input operation (s) | Subsequent input operation (s) | Short fault condition on input circuit (s) |  |  | Short fault condition on input circuit (s)
Audible Signal Devices and Visible Signal Devices within the same manually initiated fire alarm zone |  | 5 | Not Applicable | 15 |  |  | 35
Audible Signal Devices and Visible Signal Devices |  | 10 | 10 | 20 |  |  | 40
Interconnection to Signal Transmitting Unit |  | 10 | Not Applicable | Not Applicable |  |  | Not Applicable
Releasing Device Service Start of Sequence |  | 10 | Not Applicable | 20 |  |  | 40
Annunciation |  | 10 | 10 | Not Applicable |  |  | Not Applicable
Central Alarm Control Facility |  | 10 | 10 | Not Applicable |  |  | Not Applicable
Ancillary Circuit |  | 10 | 30 | Not Applicable |  |  | Not Applicable
Trouble Signal |  | 90 | 90 | Not Applicable |  |  | Not Applicable
Water Flow Devices |  | 10 | 10 | 20 |  |  | 40
NOTE 1: For the purpose of testing for response time, the determination of input operation shall be the operation of a contact device or the operation of the means to indicate a latched-in alarm condition of a smoke detector (e.g. operation of local LED)
NOTE 2: Manually operated control activations for paging and alarm selection shall have indication to confirm output operation in a maximum of 5 s. There shall be a means of providing sensory indication to the operator within 1 s that the function has been requested.
NOTE 3: The maximum times shown are based on the initiation of the alarm condition immediately following (within 0.5 s) of the circuit fault condition. See Annex A (Informative), Explanatory Materials, A6.4.5.
NOTE 4: Manually operated control activations for paging and alarm selection shall have indication to confirm output operation in a maximum of 5 s. There shall be a means of providing sensory indication to the operator within 2 s that the function has been requested.
NOTE 5: In the columns related to testing during Circuit Fault Conditions, indicated maximum response times reflect the total time where input capabilities can be delayed by up to 10 s and output capabilities can be delayed by up to 30 s.

## 32.6 Large Scale Network System (hidden)
Section 32.6 Large Scale Network Systems
NOTE 1 : Refer to 5.4 and Section 9
A | Control units or transponders serve the same area for both input circuits and output circuits. | Yes | FALSE | No | FALSE | N/A | FALSE
B | Control units or transponders with stand alone capability have signal silence, reset, and trouble silence switches with visual indicators, degraded mode capability and stand alone capability indicators. | Yes | FALSE | No | FALSE | N/A | FALSE
C | A single open circuit fault, wire-to-wire short circuit fault, or ground fault on the network results in a trouble signal and continued alarm receipt capability at each node under these conditions | Yes | FALSE | No | FALSE | N/A | FALSE
D | Under data communication link failure condition, each control unit or transponder with stand-alone capability is capable of receiving an alarm initiation and provides output operation in the area as served by the control unit or transponder. | Yes | FALSE | No | FALSE | N/A | FALSE
E | Under multiple data communication link failure conditions which create two network segments, each control unit or transponder with degraded mode capability for each segment of the network provides the following operations:
| i) Signals operate in accordance with the system sequence of operations; | Yes | FALSE | No | FALSE | N/A | FALSE
| ii) Alert signals and alarm signals are synchronized throughout each separate network segment; | Yes | FALSE | No | FALSE | N/A | FALSE
| iii) Ancillary device controls continue to operate within each network segment; | Yes | FALSE | No | FALSE | N/A | FALSE
| iv) Acknowledge, signal silence, reset and trouble silence switches with visual indicators, degraded mode capability and stand alone capability indicators, function for each network segment. | Yes | FALSE | No | FALSE | N/A | FALSE

## 32.11, 32.12, 32.13 (hidden)
Section 32.11 Remote Trouble Signal Unit Test and Inspection
NOTE 1 : Refer to 11.3 and 32.9(o).
NOTE 2 : If the fire alarm system DOES utilize remote trouble signal unit, complete 32.11 for each remote trouble signal unit.
There are no remote trouble signal units on this system. |  |  |  | FALSE
Remote trouble signal unit location:
Remote trouble signal unit identification
A | Input wiring from control unit or transponder is supervised. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Visual trouble signal operates. |  |  |  | Yes |  | FALSE | No |  | FALSE
C | Audible trouble signal operates. |  |  |  | Yes |  | FALSE | No |  | FALSE
D | Audible trouble signal silence operates. |  |  |  | Yes |  | FALSE | No |  | FALSE
Section 32.12 Printer Test
NOTE 1 : Refer to 12.1
NOTE 2 : If the fire alarm system DOES utilize printers, complete 32.12 for each printer unit.
There are no printers on this system. .. |  |  |  | FALSE
Printer location:
Printer identification:
A | Operates as per design and specification. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Zone on each alarm initiating device is correctly printed. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
Section 32.13 Ancillary Device Circuit Test
NOTE 1 : Refer to 8.3.1(aa) and 10.2(f).
Specific type of ancillary circuit |  | Ancillary circuit powered by: |  |  | Operation of ancillary circuit confirmed |  | Method of confirmation See Annex A, A32.13
|  | FAS* Check if applicable | Others Specify
[5 empty] | YES | NO
|  | FALSE |  |  | FALSE | FALSE
|  | FALSE |  |  | FALSE | FALSE
|  | FALSE |  |  | FALSE | FALSE
|  | FALSE |  |  | FALSE | FALSE
|  | FALSE |  |  | FALSE | FALSE
|  | FALSE |  |  | FALSE | FALSE
|  | FALSE |  |  | FALSE | FALSE
*FAS - fire alarm system
NOTE: The tests reported on this Form may not include the actual operational test of ancillary devices, except when noted in the Method of Confirmation column. See Annex A (Information), Explanatory Materials, A32.13.

## ULC Cover Page
444 William Street, Victoria, BC, V9A 3Y9
Phone: (250) 475-6077
service@cantec.ca
www.cantec.ca
2025
ANNUAL FIRE ALARM SYSTEM INSPECTION & TESTING RECORD
|  | Prepared for: | 0
|  | Building Address: | 1234
|  | Building Name: | TEST
|  | Date: | 2025-01-12
Please be advised that Cantec Fire Alarms Ltd. is once again an authorized dealer for Mircom. Please don’t hesitate to reach out and inquire about this partnership and what it it offers you, our client.
FPABC Cantec Fire Alarms Ltd. is a proud and contributing member to the Fire Protection Association of British Columbia since 2020.
This is to certify that the Alarm Service Company is included by Underwriters Laboratories Inc. (UL) in its Product Directories as eligible to use the UL Listing Mark in connection with Certificated Alarm Systems.
Cantec Fire Alarms will continue its endeavour to exceed industry standards; our annual audit requirements to remain a ULC listed Fire Alarm Service Provider, contributes to this effort. The pages containted within this report are compliant with the standards set by the 2024 BC Fire Code and Part 20 "Annual Fire Alarm System Test and Inspection Record" CAN/ULC S536-19 (Inlcuding Revision 1)

## EXT only
Annual Fire Extinguisher Inspection Log
NOTE: Fire Extinguishers are to be maintained in accordance with NFPA #10
| Date: | 2025-01-12 |  |  | Address: | 1234
ACTIVITY LEGEND | [5 empty] | RP | Repaired
3 | Tested | TO | Tested by Others | ND | No Device | R | Replaced | Extinguisher is outside of NFPA standards. Replace next service date with new.
F | Failed | NA | No Access | NT | Not Tested | RB | Replaced Battery
ACT | LOCATION |  | UNIT TYPE | LAST SERVICE | NEXT SERVICE | NOTE LEGEND
Glass Cabinet Dimensions
EXTs on Full Report - Automated Processor

## ELU only
Annual Emergency Lighting Unit Log
NOTE: Emergency Lighting Units shall be maintained in accordance with the 2024 BC Fire Code
NOTE 2: Canadian Electrical codes are referenced within BC Fire Code CSA C22.1:24 & CSA C282-15
| Date: | 2025-01-12 |  |  | Address: | 1234
ACTIVITY LEGEND | [5 empty] | RP | Repaired
3 | Tested | TO | Tested by Others | ND | No Device | R | Replaced
F | Failed | NA | No Access | NT | Not Tested | RB | Replaced Battery
EMERGENCY LIGHTING REPORT - CAN/ULC C282M
ACT | LOCATION |  | UNIT TYPE | BATTERY TYPE | LAST NEW BATTERY | NOTE LEGEND
ELUs on Full Report - Automated Processor

## 20.1 ¦ Report
ANNUAL FIRE ALARM SYSTEM TEST AND INSPECTION RECORD
20.1 Fire Alarm System Annual Test and Inspection Report
| Inspection Date (DD/MMM/YYYY): |  |  |  | 2025-01-12 | [10 empty] | CM
Report Revision Date (DD/MMM/YYYY):
| Building Name: |  |  |  | TEST | [10 empty] | CS
|  |  |  | Address: | 1234
|  |  |  | City, Province, Postal Code: | [11 empty] | AB
Building owner or representative's name:
| System manufacturer: | [14 empty] | JG
Model number:
| System provides: |  | FALSE | Single Stage Operation |  | FALSE | Two Stage Operation
| FALSE | Other (describe special operation):
| The fire alarm system is connected to a fire signal receiving centre | [7 empty] | Yes |  | FALSE |  | No |  | FALSE
name, if applicable:
| This Report comprises of |  | ? | pages
JM
| The entire fire alarm system has been inspected and tested in accordance with CAN/ULC-S536:2019, Inspection and Testing of Fire Alarm Systems | [7 empty] | Yes |  | FALSE |  | No |  | FALSE
| The fire alarm system is fully functional. | [7 empty] | Yes |  | FALSE |  | No |  | FALSE | JH
| During the Annual Inspection and Test were any Deficiencies Identified? See Page 2, if applicable. | [7 empty] | Yes |  | FALSE |  | No |  | FALSE
As of the following Date (M/D/Y) all identified Deficiencies have been corrected:
| During the Annual Inspection and Test were any Recommendations Identified? See Page 3, if applicable. | [7 empty] | Yes |  | FALSE |  | No |  | FALSE
The following person is responsible for ensuring that the information contained in this Test and Inspection Report is correct and complete:
Printed Name:
Certificate/ID Number (short formed)
Signature (This certifies that the information contained in this Fire Alarm System Annual Test and Inspection Report is correct and complete)
| Company Conducting Test: | [6 empty] | Cantec Fire Alarms Ltd.
| Company Phone Number: | [6 empty] | 1 (250) 475-6077
| Was there a secondary person who conducted the Test and Inspection? | [6 empty] | Yes |  | FALSE |  | No |  | FALSE
Printed Name:
Certificate/ID Number (short formed)
Signature (This certifies that the information contained in this Fire Alarm System Annual Test and Inspection Report is correct and complete)
| Company Conducting Test: | [6 empty] | Cantec Fire Alarms Ltd.
| Company Phone Number: | [6 empty] | 1 (250) 475-6077
Note on F7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Linked to cover page, 33.2 device, 33.5 signalling
Note on F9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Linked to cover page, 33.2 device, 33.5 signalling
Note on F10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Linked to cover page, 33.2 device, 33.5 signalling
Note on F12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Linked to cover page

## 20.2 ¦ Deficiencies
20.2 Deficiencies
NOTE: System and device installation locations may differ from those described in CAN/ULC-S524 if a performance based design and alternate solution documents were submitted and approved by the authority having jurisdiction for the system under test.
The Inspection and Testing of any corrections/repairs of deficiencies noted on this form has been completed by qualified personnel in the column marked "Technician Name & Certificate No.” – page 2
Item # | Device type | Device location | Deficiency | CAN/ULC-S536 Standard reference clause | Date corrected (M/D/Y) | Work order or reference no. | Company which corrected deficiency | Technician name & certificate no.
1
2
3
4
5
6
7
8
9
10
I understand that all Deficiencies noted in the table above have been corrected:
Building Owner / Owner's Representative Name:
Building Owner / Owner's Representative Signature:
Date of Signature:
NOTE: Only the above table needs to be updated on correction of deficiencies. The entire report does not have to be reissued.
CM

## 20.3 ¦ Recommendations
20.3 Recommendations
Recommendations - page 3
20.4 Technician Attendance Log
NOTE: See 7.4
Date (MM/DD/YY) | Time in / Time out | Notes (for the day) | Primary technician printed name |  | Primary technician certification no.
Note
Recommendations |  |  |  | Deficiencies
20.3.1: For the purpose of this standard, Recommendation is a proposal or suggestion as to the best course of action for improvement of system components or system operation / installations, including safety considerations, such as: |  |  |  | 20.2.1: For the purpose of this Standard, deficiency refers to a device or function that: a) Does not operate as intended b) Due to alteration in the building layout or contents, is installed in a location which is not readily accessible for service, testing, maintenance purposes due to safety considerations, and was not tested in the last 24 months; c) Is installed in an environment which is not compatible with the documented operating conditions of the specific device; or d) is installed in an orientation or location not specifically indicated by the installation instruction of the specific device.
a) Identifying antiquated or obsolete equipment; b) Availability of newer cost effective technology; or c) Alternate methods of detection.

## 21 ¦ Documentation
21 Documentation
NOTE: See Section 7. Documentation
21.1 Documentation for the fire alarm system is available or accessible on site and includes the following description of the fire alarm system:
A | Instructions for resetting the system and silencing alarm signals. | Yes |  | FALSE | No |  | FALSE
B | Instructions for silencing the trouble signal and action to be taken when the trouble signal sounds. | Yes |  | FALSE | No |  | FALSE
C | Description of the function of each operating control and indicator on the fire alarm unit. | Yes |  | FALSE | No |  | FALSE
D | Description of the area or fire zone protected by each alarm detection circuit (this may be in the form of a list or plan drawing). | Yes |  | FALSE | No |  | FALSE
E | Description of alarm signal operation. | Yes |  | FALSE | No |  | FALSE
F | Description of ancillary equipment controlled by the fire alarm system. | Yes |  | FALSE | No |  | FALSE
G | In systems that provide logical control of a smoke control system, documentation is on site and includes a sequence of operation of the smoke control system. | Yes | FALSE | No | FALSE | N/A | FALSE
H | Building diagrams are on site that clearly indicate the type and location of all smoke-control equipment (fans, dampers, etc.). | Yes | FALSE | No | FALSE | N/A | FALSE
I | Description of the fire alarm system: i) Sequence of operation (see Annex D) | Yes |  | FALSE | No |  | FALSE
| ii) Operating instruction (see Annex D) | Yes |  | FALSE | No |  | FALSE
| iii) Description of each type of field device | Yes |  | FALSE | No |  | FALSE
| iv) Details of input to programmed output functions for programmed systems | Yes |  | FALSE | No |  | FALSE
| v) Connection to a fire signal receiving centre, if required by applicable codes and regulations | Yes |  | FALSE | No |  | FALSE
| vi) Previous verification report(s) and all documentation related to any modification showing approval of such modifications by the AHJ, if applicable | Yes | FALSE | No | FALSE | N/A | FALSE
| vii) The as-built drawings of the building fire alarm system (See Annex D) | Yes |  | FALSE | No |  | FALSE
| viii) Copy of the site specific software (if applicable) | Yes | FALSE | No | FALSE | N/A | FALSE
J | Indicate location(s)and media type(s) of documentation:

## 29, 30, 31 Documentation (2) (hidden)
Part 29 Documentation
A | Instructions for resetting the system and silencing alarm signals. |  |  | Yes |  | FALSE | No |  | FALSE
B | Instructions for silencing the trouble signal and action to be taken when the trouble signal sounds. |  |  | Yes |  | FALSE | No |  | FALSE
C | Description of the function of each operating control and indicator on the fire alarm unit. |  |  | Yes |  | FALSE | No |  | FALSE
| Description of the area or fire zone protected by each alarm detection circuit (this may be in the form of a list or plan drawing). |  |  | Yes |  | FALSE | No |  | FALSE
E | Description of alarm signal operation. |  |  | Yes |  | FALSE | No |  | FALSE
F | Description of ancillary equipment controlled by the fire alarm system. |  |  | Yes |  | FALSE | No |  | FALSE
G | In systems that provide logical control of a smoke control system, documentation is on site and includes a sequence of operation of the smoke control system. |  |  | Yes |  | FALSE | No |  | FALSE
H | Building diagrams are on site that clearly indicate the type and location of all smoke-control equipment (fans, dampers, etc.). |  |  | Yes |  | FALSE | No |  | FALSE
I | Description of the fire alarm system: i) Sequence of operation (see 5.9) |  |  | Yes |  | FALSE | No |  | FALSE
| ii) Operating instruction (see 5.9) |  |  | Yes |  | FALSE | No |  | FALSE
| iii) Description of each type of field device |  |  | Yes |  | FALSE | No |  | FALSE
| iv) Details of input to programmed output functions for programmed systems; |  |  | Yes |  | FALSE | No |  | FALSE
| v) Connection to a fire signal receiving centre, if required by applicable codes and regulations; |  |  | Yes |  | FALSE | No |  | FALSE
| vi) Previous verification report(s) if applicable; |  |  | Yes |  | FALSE | No |  | FALSE
| vii) The as-built drawings of the building fire alarm system (See Annex D) |  |  | Yes |  | FALSE | No |  | FALSE
| viii) Copy of the site specific software (if applicable) |  |  | Yes |  | FALSE | No |  | FALSE
J | Indicate location and format of documentation:
Part 30 Individual Field Device, Related Circuits and Circuit Fault Tolerance
YES = Tested correctly |  | NO = Did not test correctly | N/A = Not Applicable
|  | (Refer to deficiencies 28.2) | Function or feature not provided on this fire alarm system
A | Correct field termination, conductor type and wire gauge, in accordance with CSA C22.1, Canadian Electrical Code, Section 32. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Correct field termination, conductor type and wire gauge, in accordance with equipment manufacturer's installation instructions at all system termination points. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Correct circuit polarities. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | An open circuit fault on a conventional device circuit causes a trouble signal. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Removal of any active or supporting field device circuit causes a trouble signal. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | One contact device and one non-contact device tested for operation and annunciation at the control unit or transponder, when using a field verifying device. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Class A circuits serving conventional field devices tested for the capability of providing an alarm signal on each side of an open circuit fault connection at an electrically remote point in the circuit. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Ground fault indications occur when tested at the electrically furthest field device, and do not result in normal to off-normal status change conditions. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Field device at the electrically further point from the power source (in every circuit) receives rated power in accordance with manufacturer's specifications. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Replaceable over-current devices are of correct rating. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
K | Where multiple strand optical fibre cable is not dedicated to the fire alarm system, the fire alarm system continues to function as required despite any impairment to other systems which share the cable. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Confirm circuit fault tolerance operation under OPEN CIRCUIT FAULT conditions (Record individual operation in 33.2, Individual Device Record and 33.4, Circuit Fault Tolerance Test Sheet) |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Confirm circuit fault tolerance operation under SHORT CIRCUIT FAULT conditions (Record Individual operation in 33.2, Individual Device Record and 33.4, Circuit Fault Tolerance Test Sheet) |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
N | Confirm circuit fault tolerance operation under GROUND FAULT conditions (Record Individual operation in 33.2, Individual Device Record and 33.4, Circuit Fault Tolerance Test Sheet) |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
O | Where suite fault isolators are provided, confirm in-suite signal circuit fault tolerance operation under SHORT CIRCUIT FAULT conditions (Record Individual operation in 33.2, Individual Device Record and 33.4, Circuit Fault Tolerance Test Sheet). |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
P | Under an alarm condition, confirm device operation on the source side of each shorted residential suite isolator module. (Confirm individual operation in 33.2, Individual Device Record and 33.4, Circuit Fault Tolerance Test Sheet). |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
Q | Where voice communication systems are used to broadcast messages not related to life safety (e.g. general paging), fault detection for signaling busses or circuits is maintained while broadcasting. (Confirm operation in 32.4, Non-life Safety Message Circuit Supervision Test). |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
Part 31 Operation Test Circuit Fault Tolerance
Control unit or transponder location:
Control unit or transponder identification:
Data communication link identification:
A | Each system abnormal condition specified in Table 3.1, Abnormal System Conditions, tested for each data communication link at the control unit or transponder |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Tests for alarm and trouble received under a single ground fault condition conducted on each conductor of that data communication link independently. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Each conductor in a data communications link, Class A (DCLA) tested for the capability of providing an alarm signal on each side of a single open circuit fault condition. |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | Where data communication link(s) are installed without fault isolation, impose a wire-to-wire short circuit fault on each data communication link during an non-fire alarm condition and confirm receipt of trouble and alarm condition for, each adjacent data communication link (Record results in 33.4, Circuit Fault Tolerance Test Sheet). |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Where fault isolators are installed in data communication links serving field devices, impose wire-to-wire short on the isolated side during non-fire alarm condition, confirm annunciation of the fault, and then operate a device on the source side, and confirm activation at the control unit or transponder (Record results in 33.4, Circuit Fault Tolerance Test Sheet). |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Where fault isolation in data communication links is provided between control units or transponders, the field wiring shorted between each pair of control units or transponders, in turn, annunciation of the fault confirmed and operation outside the shorted section confirmed. (Record results in 33.4, Circuit Fault Tolerance Test Sheet). |  |  | Yes | FALSE | No | FALSE | N/A | FALSE

## 22.1 ¦ CU or Transp Insp
22 Control Unit or Transponder Inspection
| YES | FALSE | = Operated Correctly | NO | FALSE | = Did not operate correctly | N/A | FALSE | = Not applicable
|  |  |  | (Refer to Deficiencies, 20.2) |  |  | Function or feature not provided on this fire alarm system
22.1 Control Unit or Transponder Inspection
NOTE 1 : See Clause 8.2 in CAN/ULC-S536-19
NOTE 2: Complete section for each control unit or transponder.
Control unit or transponder location:
Control unit or transponder identification:
A |  | Input circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Output circuit designations correctly identified in relation to connected field devices. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Correct designations for common control functions and indicators. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
D |  | Plug-in components and modules securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
E |  | Plug-in cables securely in place. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
F |  | (i) Record the date, revision and version of firmware. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
|  | (ii) Record the date, revision and version of software program. | [6 empty] | Date:
[9 empty] | Rev: |  |  | Ver:
G |  | Control unit and transponder are clean and free of dust and dirt. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Fuses in accordance with manufacturer's specification. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Control unit or transponder lock functional. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Termination points from wiring to field devices secure. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE

## 32 ControlUnit¦Transponder (2) (hidden)
Part 32 Control Unit or Transponder Record
Section 32.1 Control Unit or Transponder
NOTE 1 : Refer to 5.4 and 8.2
NOTE 2: Complete section for each control unit or transponder.
Control unit or transponder location:
Control unit or transponder identification:
A | Input circuit designations correctly identified in relation to connected field devices. | Yes | FALSE | No | FALSE | N/A | FALSE
B | Output circuit designations correctly identified in relation to connected field devices. | Yes | FALSE | No | FALSE | N/A | FALSE
C | Correct designations for common control functions and indicators. | Yes | FALSE | No | FALSE | N/A | FALSE
D | Plug-in components and modules securely in place. | Yes | FALSE | No | FALSE | N/A | FALSE
E | Plug-in cables securely in place. | Yes | FALSE | No | FALSE | N/A | FALSE
F | Record the date, revision and version of firmware and software program. | Date:
|  | Rev: |  |  | Ver:
G | Control unit and transponder are clean and free of dust and dirt. | Yes | FALSE | No | FALSE | N/A | FALSE
H | Fuses in accordance with manufacturer's specification. | Yes | FALSE | No | FALSE | N/A | FALSE
I | Control unit or transponder lock functional. | Yes | FALSE | No | FALSE | N/A | FALSE
J | Termination points from wiring to field devices secure. | Yes | FALSE | No | FALSE | N/A | FALSE
K | Control unit or transponder power disconnects in accordance with CSA C22.1, Safety Standard for Electrical Installations, Canadian Electrical Code, Part 1. | Yes | FALSE | No | FALSE | N/A | FALSE
L | Field wiring entry points for the various circuits and circuit separations are in accordance with the manufacturer's installation instructions | Yes | FALSE | No | FALSE | N/A | FALSE
M | Main power supply feed wiring in accordance with manufacturer's specifications. | Yes | FALSE | No | FALSE | N/A | FALSE
N | Control units or transponders with stand alone capability serves the same area for both input circuits and output circuits. | Yes | FALSE | No | FALSE | N/A | FALSE
O | Control units or transponders which operate with stand alone capability have signal silence, reset, and trouble silence switches with visual indicators, degraded mode capability and stand alone capability indicators. | Yes | FALSE | No | FALSE | N/A | FALSE
P | Each control unit or transponder furnished with operating and maintenance instructions, and installation instructions | Yes | FALSE | No | FALSE | N/A | FALSE
Q | Control unit or transponder visual indicators comply with Table 8.1, Visual Indicators-Colour Code. | Yes | FALSE | No | FALSE | N/A | FALSE
Section 32.2 Control Unit or Transponder Test
CM
NOTE 1 : Refer to 5.4, 8.3.1 and 7.1
NOTE 2: Complete section for each control unit or transponder.
Control unit or transponder location:
Control unit or transponder identification:
A | Power 'ON' visual indicator operates. | Yes | FALSE | No | FALSE
B | Time and date indication corresponds with local time and date. | Yes | FALSE | No | FALSE | N/A | FALSE
C | Common visual trouble signal operates. | Yes | FALSE | No | FALSE
D | Common audible trouble signal operates. | Yes | FALSE | No | FALSE | N/A | FALSE
E | Trouble signal silence switch operates. | Yes | FALSE | No | FALSE | N/A | FALSE
F | Main power supply failure trouble signal operates. | Yes | FALSE | No | FALSE | N/A | FALSE
G | Trouble signal operates during positive and negative ground fault tests. | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alert signal operates. | Yes | FALSE | No | FALSE | N/A | FALSE
I | Alarm signal operates. | Yes | FALSE | No | FALSE | N/A | FALSE
J | Automatic transfer from alert signal to alarm signal operates. | Yes | FALSE | No | FALSE | N/A | FALSE
Time:
K | Manual transfer from alert signal to alarm signal operates. | Yes | FALSE | No | FALSE | N/A | FALSE
L | Automatic transfer from alert signal to alarm signal cancel (acknowledge) feature operates on two-stage system. | Yes | FALSE | No | FALSE | N/A | FALSE
M | Alarm signal silence inhibit function operates. | Yes | FALSE | No | FALSE | N/A | FALSE
N | Alarm signal manual silence operates. | Yes | FALSE | No | FALSE | N/A | FALSE
O | Alarm signal silence visual indication operates. | Yes | FALSE | No | FALSE | N/A | FALSE
P | Alarm signals when silenced, automatically reinitiate upon subsequent alarm from another NBC required fire alarm zone. | Yes | FALSE | No | FALSE | N/A | FALSE
Q | Duration of alarm signal prior to automatic silence. | Time: |  |  |  | N/A | FALSE
R | Audible and visual alarm signals programmed and operate per design and specification. | Yes | FALSE | No | FALSE | N/A | FALSE
S | Input circuit, alarm and supervisory operation, including audible and visual indicator operates. | Yes | FALSE | No | FALSE | N/A | FALSE
T | Input circuit supervision fault causes a trouble indication. | Yes | FALSE | No | FALSE | N/A | FALSE
U | Output circuit alarm indicators operate. | Yes | FALSE | No | FALSE | N/A | FALSE
V | Output circuit supervision fault causes a trouble indication. | Yes | FALSE | No | FALSE | N/A | FALSE
W | Visual indicator test (lamp test) operates. | Yes | FALSE | No | FALSE | N/A | FALSE
X | Coded signal sequences operate not less than the required number of times and the correct alarm signal operates thereafter. | Yes | FALSE | No | FALSE | N/A | FALSE
Y | Coded signal sequences are not interrupted by subsequent alarms. | Yes | FALSE | No | FALSE | N/A | FALSE
Z | Ancillary device by-pass results in a trouble signal. | Yes | FALSE | No | FALSE | N/A | FALSE
AA | Input circuit to output circuit operation, including ancillary device circuits for correct program operation, as per design and specification. | Yes | FALSE | No | FALSE | N/A | FALSE
BB | Fire alarm system reset operates | Yes | FALSE | No | FALSE | N/A | FALSE
Record reset time:
CC | Main power supply to emergency power supply transfer operates. | Yes | FALSE | No | FALSE | N/A | FALSE
DD | Control unit or transponder bonded to ground. | Yes | FALSE | No | FALSE | N/A | FALSE
EE | Status change confirmation feature (smoke detectors only) verified. | Yes | FALSE | No | FALSE | N/A | FALSE

## 22.2 ¦ CU or Transp Test
22.2 Control Unit or Transponder Test
See 8.3 in CAN/ULC-S536-19
Complete section for each control unit or transponder.
Control unit or transponder location: |  | 0
Control unit or transponder identification: |  | 0
A | Power 'ON' visual indicator operates. |  | Yes | FALSE | No | FALSE
B | Time and date indication corresponds with local time and date. |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Common visual trouble signal operates. |  | Yes | FALSE | No | FALSE
D | Common audible trouble signal operates. |  | Yes | FALSE | No | FALSE
E | Trouble signal silence switch operates. |  | Yes | FALSE | No | FALSE
F | Main power supply failure trouble signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Trouble signal operates during positive and negative ground fault tests. |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alert signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Automatic transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Time:
K | Manual transfer from alert signal to alarm signal operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Automatic transfer from alert signal to alarm signal cancel (acknowledge) feature operates on two-stage system. |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Alarm signal silence inhibit function operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
N | Alarm signal manual silence operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
O | Alarm signal silence visual indication operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
P | Alarm signals when silenced, automatically reinitiate upon subsequent alarm from another NBC required fire alarm zone. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Q | Duration of alarm signal prior to automatic silence. |  | Time: |  | No | FALSE | N/A | FALSE
R | Audible and visual alert signals and alarm signals programmed and operate per design and specification; or documentation as provided in Section 21. |  | Time: |  |  |  | N/A | FALSE
S | Input circuit, alarm and supervisory operation, including audible and visual indicator operates. |  | Yes | FALSE | No | FALSE
T | Input circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
U | Output circuit alarm indicators operate. |  | Yes | FALSE | No | FALSE | N/A | FALSE
V | Output circuit supervision fault causes a trouble indication. |  | Yes | FALSE | No | FALSE | N/A | FALSE
W | Visual indicator test (lamp test) operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
X | Coded signal sequences operate not less than the required number of times and the correct alarm signal operates thereafter. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Y | Coded signal sequences are not interrupted by subsequent alarms. |  | Yes | FALSE | No | FALSE | N/A | FALSE
Z | Ancillary device by-pass results in a trouble signal. |  | Yes | FALSE | No | FALSE | N/A | FALSE
AA | Input circuit to output circuit operation, including ancillary device circuits, for correct program operation, as per design and specification, or documentation as detailed in D, Description of Fire Alarm System for Inspection and Test Procedures. |  | Yes | FALSE | No | FALSE | N/A | FALSE
BB | System Reset operates |  | Yes | FALSE | No | FALSE
CC | Main power supply to emergency power supply transfer operates. |  | Yes | FALSE | No | FALSE | N/A | FALSE
DD | Smoke detector alarm verification (status change confirmation) verified. [Refer to14.4.3, Smoke Detector Alarm Verification (Status Change Confirmation)]. |  | Yes | FALSE | No | FALSE | N/A | FALSE

## 22.3 + 22.4 ¦ Voice & PS
22.3 Voice Communication Test
NOTE: See Subsection 8.5 in CAN/ULC-S536-19
|  |  | There are no Voice Communication Capabilities on this system | FALSE
A | Power 'ON' visual indicator operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Common visual trouble signal operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Common audible trouble signal operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | Trouble signal silence switch operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | All-call voice paging, including visual indicator, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Output circuits for selective voice paging, including visual indication, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Output circuits for selective voice paging trouble operation, including visual indication, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Microphone, including press to talk switch, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Operation of voice paging does not interfere with initial inhibit time of alert signal or alarm signal. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | All-call voice paging operates (on emergency power supply) |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
K | Where systems use back-up amplifiers, the automatic transfer feature operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Circuits for emergency telephone call-in operation, including audible and visual indication, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
M | Circuits for emergency telephones for operation, including two-way voice communication, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
N | Circuits for emergency telephone trouble operation, including visual indication, operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
O | Emergency telephone verbal communication operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
P | Emergency telephone operable or in-use tone at handset operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
Q | In standby mode, a short, or open on a paging, alert, alarm, or emergency telephone voice communication buss results in a buss specific trouble condition. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
22.4 Power Supply Inspection
NOTE: See Subsection 8.5 in CAN/ULC-S536-19
Control unit or transponder location: |  | 0
Control unit or transponder identification: |  | 0
Circuit disconnect means or breaker location:
Circuit disconnect means or breaker identification:
A | Fused in accordance with the manufacturer's marked rating of the system |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | The primary supply is equipped with the identified disconnect means |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Adequate to meet the requirements of the system |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | A short on the isolated side of each power isolation module results in a trouble condition |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Operation of a device on the source side of each shorted power isolation module is confirmed. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
F | Power for ancillary devices is taken from a source separate from the fire alarm system control unit or transponder power supply. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Power for ancillary devices is taken from the control unit or transponder that is designed to provide such power. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Ancillary devices, which are powered from control unit or transponder, are recorded. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE

## 32.7, 32.8 Power Supply (2) (hidden)
Section 32.7 Power Supply Inspection
NOTE 1 : Refer to 5.4, 10.1 and 10.2
NOTE 2 : Complete section for each control unit or transponder.
Control unit or transponder location:
Control unit or transponder identification:
Circuit disconnect means or breaker location:
Circuit disconnect means or breaker identification:
| Conforms with the requirements of CAN/ULC-S524, Standard for Installation of Fire Alarm Systems; and CSA C22.1, Safety Standard for Electrical Installations, Canadian Electrical Code, Part I, Section 32. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
A | Fused in accordance with the manufacturer's marked rating of the system. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B | The primary supply is equipped with the identified disconnect means. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C | Adequate to meet the requirements of the system. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
D | Power for ancillary devices is taken from a source separate from the fire alarm system control unit or transponder power supply. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
E | Power for ancillary devices is taken from the control unit or transponder that is designed to provide such power. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
F | Ancillary devices, which are powered from control unit or transponder, are recorded. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
Section 32.8 Emergency Power Supply Verification
NOTE 1 : Refer to 5.4, 10.4, 10.5, Annex C.
NOTE 2 : Complete section for each emergency power supply
Emergency power supply location:
Emergency power supply identification:
Emergency power supply provided by:
FALSE | Batteries | FALSE | Generator |  | FALSE | UPS |  | FALSE | Combination
NBC required full load alarm operation time |  | FALSE | 2 Hours |  | FALSE | 1 hour |  | FALSE | 30 min |  | FALSE | 5 min
Installed batteries Qty: |  |  | V dc: |  | Ah:
Battery Tests
(Reference: 10.4)
A | Correct battery type as recommended by manufacturer. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B | Correct battery rating as determined by battery calculations based on full system load. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C | Battery voltage with main power supply 'ON', | [6 empty] | Voltage: |  |  |  | V dc
[8 empty] | Current: |  |  |  | A
D | Battery voltage and current with main power supply 'OFF' and fire alarm system in supervisory condition. | [6 empty] | Voltage: |  |  |  | V dc
[8 empty] | Current: |  |  |  | A
E | Battery voltage and current with main power supply 'OFF' and fire alarm system in full load alarm condition. | [6 empty] | Voltage: |  |  |  | V dc
[8 empty] | Current: |  |  |  | A
F | Free of physical damage | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
G | Terminals cleaned and lubricated | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H | Terminals clamped tightly. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I | Correct electrolyte level. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J | Specific gravity of electrolyte is within manufacturer's specifications. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
K | Free of electrolyte leakage. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
L | Adequately ventilated. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
M | Battery manufacturer's date code. | [6 empty] | Date:
N | Disconnection of battery causes trouble signal at the fire alarm control unit. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
O | Indicate type of battery tests performed:
| i) Required supervisory load for 24 h followed by the required full load operation; or | [6 empty] | Yes |  | FALSE | No |  | FALSE
| ii) Silent accelerated test. (Refer to Annex C1, New Silent Accelerated Test Methods); or | [6 empty] | Yes |  | FALSE | No |  | FALSE
| iii) Battery manufacturer's methods. (Refer to Annex C1), | [6 empty] | Yes |  | FALSE | No |  | FALSE
Specify:
P | Record calculated battery capacity (Refer to Annex C2.1c) | [8 empty] | Ah
Q | Record battery terminal voltage after completion of tests. | [8 empty] | V dc
R | Confirm battery voltage not less than 85% of its rating after the tests. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
S | Battery charging current | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
Emergency Power Generator Tests
(Reference: 10.5)
A | Generator provides power to the AC Circuit serving the fire alarm system. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B | Trouble condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C | Generator Run condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
Emergency power supply identification:
D | Testing coordinated with emergency power generator tests. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
E | Low Fuel Level trouble results in an audible trouble signal and a visual indication at the required annunciator. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
Generator fueled by: |  | FALSE | Diesel | FALSE | Natural Gas | FALSE | Other:
Fuel Level | [6 empty] | % of full capacity: |  | % | Estimated run time: |  |  | Hrs.
Low Fuel Level Set-point: |  |  | FALSE | % of full capacity |  | FALSE | Gallons | FALSE | Litres

## 22.5 ¦ Power Supply(s)
22.5 Emergency Power Supply Test and Inspection
NOTE 1 : Complete section for each control unit or transponder.
Emergency power supply location:
Emergency power supply identification:
Emergency power supply provided by:
Circuit disconnect means or breaker identification:
Batteries |  | FALSE |  | Generator | FALSE | UPS | FALSE | Combination |  |  | FALSE
NBC required full load alarm operation time |  |  |  | 2 Hours | FALSE | 1 hour | FALSE | 30 min |  | FALSE | 5 min |  | FALSE
Installed batteries Qty: |  |  | V dc: |  | Ah:
BATTERY TESTS (Reference: 9.2)
A |  | Correct battery type as recommended by manufacturer. | [5 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B |  | Correct battery rating as determined by battery calculations based on full system load. | [5 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C |  | Battery voltage with main power supply 'ON', | [5 empty] | Voltage: |  |  |  | V dc
[8 empty] | Current: |  |  |  | A
D |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in supervisory condition. | [5 empty] | Voltage: |  |  |  | V dc
[8 empty] | Current: |  |  |  | A
E |  | Battery voltage and current with main power supply 'OFF' and fire alarm system in full load alarm condition. | [5 empty] | Voltage: |  |  |  | V dc
[8 empty] | Current: |  |  |  | A
F |  | Free of physical damage | [5 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
G |  | Terminals cleaned and lubricated | [5 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
H |  | Terminals clamped tightly. | [5 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
I |  | Correct electrolyte level. | [5 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
J |  | Specific gravity of electrolyte is within manufacturer's specifications. | [5 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
K |  | Battery free of electrolyte leakage. | [5 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
L |  | Adequately ventilated. | [5 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
M |  | Battery manufacturer's date code. | [5 empty] | Date:
N |  | Disconnection of battery causes trouble signal at the fire alarm control unit. | [5 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
O |  | Indicate type of battery tests performed:
|  | i) Required supervisory load for 24 h followed by the required full load operation; or | [5 empty] | Yes |  | FALSE | No |  | FALSE
|  | ii) Silent accelerated test. (Refer to Annex C1, New Silent Accelerated Test Methods); or | [5 empty] | Yes |  | FALSE | No |  | FALSE
|  | iii) Battery manufacturer's methods. (Refer to Annex C1), | [5 empty] | Yes |  | FALSE | No |  | FALSE
Specify:
P |  | Record calculated battery capacity (Refer to Annex C2.) | [7 empty] | Ah
Q |  | Record battery terminal voltage after completion of tests. | [7 empty] | V dc
R |  | Confirm battery voltage not less than 85% of its rating after the tests. | [5 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
S |  | Battery charging current | [7 empty] | A
EMERGENCY POWER GENERATOR TESTS (Reference: 9.3)
A | Generator provides power to the AC Circuit serving the fire alarm system. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
B | Trouble condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
C | Generator Run condition at the emergency generator shall result in an audible common trouble signal and a visual indication at the required annunciator. | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE

## 22.6 ¦ Annunciator(s)
22.6 Annunciator, Remote Trouble Signal Unit, Display and Control Centre Test and Inspection
NOTE 1 : See Section 10 in CAN/ULC-S536-19
NOTE 2 : Complete section for each device
Annunciator or remote trouble signal unit location:
Annunciator or remote trouble signal unit identification:
A | Power 'ON' indicator operates | Yes | FALSE | No | FALSE | N/A | FALSE
B | Individual alarm and supervisory zone designation labels are properly identified | Yes | FALSE | No | FALSE | N/A | FALSE
C | Where individual devices are annunciated confirm the individual alarm and supervisory indications are properly identified. | Yes | FALSE | No | FALSE | N/A | FALSE
D | Where active and supporting field devices are utilized, the device location and programmed device label/descriptor shall be confirmed. | Yes | FALSE | No | FALSE | N/A | FALSE
E | Common trouble signal operates. | Yes | FALSE | No | FALSE | N/A | FALSE
F | Visual indicator test (lamp test) operates. | Yes | FALSE | No | FALSE | N/A | FALSE
G | Input wiring from control unit or transponder is supervised. | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alarm signal silence visual indicator operates. | Yes | FALSE | No | FALSE | N/A | FALSE
I | I Switches for ancillary functions operate as per design and specification, or in accordance with documentation as detailed in Annex D, Description of Fire Alarm System for Inspection and Test Procedures. | Yes | FALSE | No | FALSE | N/A | FALSE
J | Other ancillary function visual indicators operate. | Yes | FALSE | No | FALSE | N/A | FALSE
K | Manual activation of alarm signal and indication operates. | Yes | FALSE | No | FALSE | N/A | FALSE
L | Displays are visible in installed location. | Yes | FALSE | No | FALSE | N/A | FALSE
M | Operates on emergency power. | Yes | FALSE | No | FALSE | N/A | FALSE

## 22.7 ¦ Annun & Seq Disp
22.7 Annunciator or Sequential Display
NOTE 1 : See 10.2 in CAN/ULC-S536-19
NOTE 2 : If the fire alarm system DOES utilize remote annunciators, complete 22.7 for each annunciator or sequential display
|  |  | There are no annunciators or sequential displays on this system. | FALSE
Annunciator or sequential display location: |  | 0
Annunciator or sequential display identification: |  | 0
A | Power 'ON' indicator operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
B | Individual alarm and supervisory zone designation labels are properly identified. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
C | Where individual devices are also annunciated confirm the individual alarm and supervisory indications are properly identified. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
D | Where active and supporting field devices are utilized, the device location and programmed device label/descriptor shall be confirmed. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
E | Common trouble signal operates. |  |  |  | Yes | FALSE | No | FALSE
F | Visual indicator test (lamp test) operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
G | Input wiring from control unit or transponder is supervised. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
H | Alarm signal silence visual indicator operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
I | Switches for ancillary functions operate as per design and specification, or in accordance with documentation as detailed in Section 21. (See section 7.) |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
J | Ancillary function visual indicators operate. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
K | Manual activation of alarm signal and indication operates. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
L | Displays are visible in installed location. |  |  |  | Yes | FALSE | No | FALSE
M | Multi-line sequential display operates as per 10.2, where utilized. |  |  |  | Yes | FALSE | No | FALSE | N/A | FALSE
22.8 Remote Trouble Signal Unit Test and Inspection
NOTE : If the fire alarm system DOES utilize remote trouble signal unit, complete 22.8 for each remote trouble signal unit
|  |  | There are no remote trouble signal units on this system. | FALSE
Remote trouble signal unit location:
Remote trouble signal unit identification:
A | Input wiring from control unit or transponder is supervised. |  |  |  | Yes |  | FALSE | No |  | FALSE
B | Visual trouble signal operates. |  |  |  | Yes |  | FALSE | No |  | FALSE
C | Audible trouble signal operates. |  |  |  | Yes |  | FALSE | No |  | FALSE
D | Audible trouble signal silence operates. |  |  |  | Yes |  | FALSE | No |  | FALSE

## 22.9 + 22.10 ¦ Printer
22.9 Printer Test
NOTE: If the fire alarm system DOES utilize printers, complete 22.9 for each printer unit.
|  |  |  | There are no printers on this system | FALSE
Printer location :
Printer identification :
A | Operates as per design and specification, or in accordance with documentation as detailed in Annex D, Description of Fire Alarm System for Inspection and Test Procedures. | [6 empty] | Yes |  | FALSE | No |  | FALSE
B | Zone of each alarm initiating device is correctly printed | [6 empty] | Yes |  | FALSE | No |  | FALSE
22.10 Ancillary Device Circuit Test
Specific type of ancillary circuit |  | Ancillary circuit powered by : |  | Operation of ancillary circuit confirmed |  |  |  | Method of confirmation See Annex A, A22.10
|  | FACU* Check if applicable | Others specify
|  | FALSE |  | Yes | FALSE | No | FALSE
|  | FALSE |  | Yes | FALSE | No | FALSE
|  | FALSE |  | Yes | FALSE | No | FALSE
|  | FALSE |  | Yes | FALSE | No | FALSE
|  | FALSE |  | Yes | FALSE | No | FALSE
|  | FALSE |  | Yes | FALSE | No | FALSE
*FACU - fire alarm control unit
NOTE: The tests reported on this Form may not include the actual operational test of ancillary devices, except when noted in the Method of Confirmation column. See Annex A, A22.10.
22.11 Interconnection to the Fire Signal Receiving Centre
NOTE: If the fire alarm system DOES have an interconnection to the fire signal receiving centre, complete 22.11 for each transmitter.
[6 empty] | There are no interconnections to a Fire Signal Receiving Centre on this system. | FALSE
A | The fire signal receiving centre transmitter is integral to the fire alarm control unit. | [6 empty] | Yes |  | FALSE | No |  | FALSE
B | Receipt of the alarm transmission to the fire signal receiving centre. | [6 empty] | Yes |  | FALSE | No |  | FALSE
C | Receipt of the supervisory transmission to the fire signal receiving centre | [6 empty] | Yes | FALSE | No | FALSE | N/A | FALSE
D | Receipt of the trouble transmission to the fire signal receiving centre | [6 empty] | Yes |  | FALSE | No |  | FALSE
E | Disabling or disconnecting the fire signal receiving centre transmitter results in a specific trouble signal at the control unit or transmitter and also transmits a trouble signal to the fire signal receiving centre. | [6 empty] | Yes |  | FALSE | No |  | FALSE
F | Disabling or disconnecting the fire signal receiving centre transmitter transmits a trouble signal to the fire signal receiving centre. | [6 empty] | Yes |  | FALSE | No |  | FALSE
G | Output circuits for selective voice paging trouble operation, including visual indication, operates. | [6 empty] | Name :
Telephone :
H | Operation of the fire signal receiving centre disconnect means transmits trouble to the fire signal receiving centre. | [6 empty] | Yes |  | FALSE | No |  | FALSE

## 23.1 Field Device Legend
23 Field Device Records
23.1 Field Device Testing – Legend and Notes
NOTE: Add additional line items for each additional type and/or model number of devices forming part of the fire alarm system as necessary to this Legend
Device type | Description | Type | Model no.
M | Manual Station
RHT | Heat Detector, Restorable
HT | Heat Detector, Non-Restorable
S | Smoke Detector
| Sensitivity Test Method or Test Equipment: | Not applicable | Not applicable
Model/Method:
| Manufacturer Sensitivity Range: | Not applicable | Not applicable
Note: CAN/ULC-S529 required range is 0.5 to 4.0 %/ft obscuration. Recorded sensitivity measurement units may not be in %/ft depending upon the testing method used.
SB | Sounder Base
RI | Remote Indicator Unit
DS | Duct Smoke detector
-- | Other Type of Detector
SFD | Supporting Field Device (Monitor)
FS | Sprinkler Flow Switch
SS | Sprinkler Supervisory device
-- | Other Supervisory Devices (Low Pressure, Low Water, Low Temperature, Power Loss, etc.)
EM | Fault Isolator
B | Bell
H | Horn
V | Visible Signal Device
SP | Cone Type Speaker
HSP | Horn Type Speaker
SSS | Suite Silence Switch
SSAD | Suite Silence Audible Device
AD | Ancillary Device
ET | Emergency Telephone
EOL | End-of-Line Device
NOTE: Refer to Section 14, Field Devices.
Notes continue onto next page…
23.1.1 The following notes apply to 23.2, Individual Device Record
NOTE 1: | Smoke detector sensitivity reading confirmed by the control panel or measurement obtained through testing to be recorded in the measurements column
NOTE 2: | Smoke detector cleaning or replacement date should also be recorded in the comments column.
NOTE 3: | Status change, including time delay, should be recorded in the measurements column.
NOTE 4: | Duct smoke detector pressure differential should be confirmed and recorded in the measurements column.
NOTE 5: | Transport time of air sampling type detector to be confirmed and recorded in the measurements column
NOTE 6: | Time delay setting of water flow switch should be recorded in the measurements column.
NOTE 7: | Sprinkler supervisory switches cause supervisory condition to be annunciated but not an alarm condition.
NOTE 8: | Upper and lower pressure setting of supervisory devices should be recorded in the measurements column.
NOTE 9: | Low temperature setting should be recorded in the measurements column.
NOTE 10: | Identify the specific ancillary devices in the measurements column.
NOTE 11: | Identify date field device operation (e.g., alarm, trouble, supervisory, annunciation indication).
NOTE 12: | Identify zone, circuit number, or address.
NOTE 13: | Identify conventional field device locations.
NOTE 14: | Identify active field device and supporting field device, data communication link (DCL), address and location.
NOTE 15: | a) Test and confirm conventional field device supervision of wiring via open circuit fault
b) Test and confirm active and supporting field device supervision via absence of device.
NOTE 16: | Confirm field device free of damage.
NOTE 17: | Confirm field device free of foreign substance.
NOTE 18: | Confirm field device mechanically supported independently of the wiring.
NOTE 19: | Confirm field device protective dust shields or covers removed.
NOTE 20: | "Correctly installed" refers to the Version of CAN/ULC-S524, Standard for the Installation fo Fire Alarm Systems, applicable at the time of intstallation of the system or device beign tested.
NOTE 21: | Smoke Detectors that employ sounder bases or activate local audible signaling device(s), used in lieu of smoke alarms, to be tested to confirm local sounder operation and annunciation at the control panel, including visible device operation, as applicable, and individually recorded.
NOTE 22: | When batteries are replaced in the short-range radio frequency (wireless) devices, battery replacement date to be identified in the comments section.

## 23.2 Device Record
Section 33.2 Individual Device Record
NOTE: Device type can be expressed as an abbreviation per 23.1, Field Device Testing - Legend and Notes.
NOTE: All Sprinkler Devices, please refer to the Sprinkler System Report
Building Name: | TEST | [7 empty] | Date (DD/MMM/YYYY): |  | 2025-01-12
Additional Device Legend for devices not included in Section 23.1 Field Device Legend of CAN/ULC S536-19
BZB: Sounder Base | GA: General Alarm | LA: Low Air Signal |  |  | DH: Door Holder | [5 empty] | RI: Remote Indicator
H/V: Horn Strobe Combo | ISO: Isolator | PL: Power Loss |  |  | FHT: Fixed Temp Heat Detector | [5 empty] | S/CO: Smoke/CO Combo Detector
SP: Cone Type Speaker | RHT/S: Heat/Smoke Detector Combo | TS: Tamper Switch |  |  | HHT: High Heat Detector (Non-Rest.) | [5 empty] | ISO: Isolator (A: Audible, D: Data Loop)
MOD: Module (R, 2, R6, 10, M, CR) | RI: Remote Indicator | SW: Silencing Switch |  |  | AD: Ancillirary Device | [5 empty] | SA + (Add ons): Smoke Alarms
Device Location | Annunciated Device Label/LCD Text (If applicable) | Device Type (or abbreviation) | Requires Service or Missing | Circuit Number or Device Address | Annunciated FIRE ZONE | Correctly Installed (Y/N) | Measurements | Alarm/Activation Confirmed | Annunciator Indication | Supervised Circuit Trouble Signal | General Alarm Circuit (if applicable) | Remarks (Smoke Alarm due dates) |  |  |  | Fire Alarm Device Look Up Table
[13 empty] | DATA VALIDATION |  |  | R (Device Type) | AA (G Output) | AB (I Output) | AC (J Output) | AD (K Output)
[13 empty] | ✔ | Y | YES | M | Y | ✔ | ✔ | ✔
[13 empty] | ✖ | N |  | RHT | Y | ✔ | ✔ | ✔
[13 empty] | N/A |  |  | HT | Y | ✔ | ✔ | ✔
[16 empty] | S | Y | ✔ | ✔ | ✔
[16 empty] | SB | Y | ✔ | ✔ | ✔
[16 empty] | RI | Y | ✔ | ✔ | ✔
[16 empty] | DS | Y | ✔ | ✔ | ✔
[16 empty] | SFD | Y | ✔ | ✔ | ✔
[16 empty] | FS | Y | ✔ | ✔ | ✔
[16 empty] | SS | Y | ✔ | ✔ | ✔
[16 empty] | EM | Y | ✔ | ✔ | ✔
[16 empty] | B | Y | ✔ | ✔ | ✔
[16 empty] | H | Y | ✔ | ✔ | ✔
[16 empty] | V | Y | ✔ | ✔ | ✔
[16 empty] | SP | Y | ✔ | ✔ | ✔
[16 empty] | HSP | Y | ✔ | ✔ | ✔
[16 empty] | SSS | Y | ✔ | ✔ | ✔
[16 empty] | SSAD | Y | ✔ | ✔ | ✔
[16 empty] | AD | Y | ✔ | ✔ | ✔
[16 empty] | ET | Y | ✔ | ✔ | ✔
[16 empty] | EOL | Y | ✔ | ✔ | ✔
[16 empty] | RHT/S | Y | ✔ | ✔ | ✔
[16 empty] | BZ | Y | ✔ | ✔ | ✔
[16 empty] | H/V | Y | ✔ | ✔ | ✔
[16 empty] | SP | Y | ✔ | ✔ | ✔
[16 empty] | DH | Y | ✔ | ✔ | ✔
[16 empty] | FHT | Y | ✔ | ✔ | ✔
[16 empty] | GA | Y | ✔ | ✔ | ✔
[16 empty] | HHT | Y | ✔ | ✔ | ✔
[16 empty] | MAG | Y | ✔ | ✔ | ✔ | SA","SAA" "SAAB","SAB", "SAPA" SAPAB","SAPB","SACOA","SACOB","SACOAB", "SAPCOA", "SAPCOB","SAPCOB","SAPCOAB","
[16 empty] | MOD-R | Y | ✔ | ✔ | ✔ | SAA | SACOA | SALi | SAAR | SAPCOLi | SAPALiV
[16 empty] | MOD-2 | Y | ✔ | ✔ | ✔ | SAAB | SACOB | SAALi | SAABR | SACOALi | SAALiV
[16 empty] | MOD-R6 | Y | ✔ | ✔ | ✔ | SAB | SACOAB | SAPLi | SAPABR |  | SAAV
[16 empty] | MOD | Y | ✔ | ✔ | ✔ | SAPA | SAPCOA |  |  |  | SAPAV
[16 empty] | SFD | Y | ✔ | ✔ | ✔ | SAPAB | SAPCOAB |  |  |  | SAPABV
[16 empty] | LA | Y | ✔ | ✔ | ✔ | SAPB | SAPCOB |  |  |  | SAABV
[16 empty] | TS | Y | ✔ | ✔ | ✔
[16 empty] | ISO | Y
[16 empty] | ISO-A | Y |  |  |  | SALi", "SAALi","SAPLi","SAAR","SAPABR","SAABR","SAPCOLi" "SACOALi" "SAALiV","SAPALiV","SAAV","SAPAV","SAPABV","SAABV"
[16 empty] | ISO-D | Y
[16 empty] | SAPB | Y |  |  |  | BASE | IF CO | IF RELAY ADDED | IF STROBE
[16 empty] | SAB | Y |  |  |  | SAA | SACOA | SAAR | SAAV
[16 empty] | SAA | Y |  |  |  | SAAB | SACOAB | SAABR | SAABV
[16 empty] | SAAB | Y |  |  |  | SAPA | SAPCOA | SAPAR | SAPAV
[16 empty] | SAPA | Y |  |  |  | SAPAB | SAPCOAB | SAPABR | SAPABV
[16 empty] | SAPAB | Y |  |  |  | SALi | SACOALi
[16 empty] | SALi | Y |  |  |  | SAALi | SAPCOLi |  | SAALiV
[16 empty] | SAALi | Y |  |  |  | SAPLi
[16 empty] | SAPLi | Y |  |  |  | SAPALi |  |  | SAPALiV
[16 empty] | SAPALi | Y
[16 empty] | SACOA | Y
[16 empty] | SACOAB | Y
[16 empty] | SAPCOA | Y
[16 empty] | SAPCOAB | Y
[16 empty] | SACOALi | Y
[16 empty] | SAPCOLi | Y
[16 empty] | SAAR | Y
[16 empty] | SAABR | Y
[16 empty] | SAPAR | Y
[16 empty] | SAPABR | Y
[16 empty] | SAAV | Y
[16 empty] | SAABV | Y
[16 empty] | SAPAV | Y
[16 empty] | SAPABV | Y
[16 empty] | SAALiV | Y
[16 empty] | SAPALiV | Y
[16 empty] | SALi | Y
[16 empty] | SAALi | Y
[16 empty] | SAPLi | Y
[16 empty] | SAPCOB | Y
Note on A13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Text will wrap
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Text will wrap
Note on E13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Formatted as text so numbers stay as you enter them. Especially helpful for addresses
Note on F13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Formatted as text so numbers stay as you enter them. Especially helpful for addresses
Note on H13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Formatted as text so numbers stay as you enter them. Especially helpful for addresses
Note on M13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Text will wrap

## 23.3 CircuitFaultTolerance
Section 33.3 Subsequent Alarm (Alarm Resound) Control Panel Test Sheet
NOTE 1 : Refer to 8.3.1(o)
Initial fire alarm input zone test location |  | Field device label |  | subsequent alarm activation test (following alarm signal silence) |  |  | Field device label | Alarm signals remain silent |  | Note: If signals re-activated following signal silence - in result of fire alarm device
Identify NBC zone designation where initial fire alarm condition was activated |  | Identify fire alarm device used to initiate fire alarm signals activation |  | Identify NBC zone designation where subsequent fire alarm device was activated following alarm signal silence |  |  | Identify subsequent fire alarm device activated in same NBC zone following signal silence | Yes | No | Record system deficiency in Section 28.2, Deficiencies
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
[8 empty] | FALSE | FALSE
NOTE: Where devices are added to an existing system which was designed and approved with a different sequence of re-sounding operation and the operation of the new devices conform to the original sequence of operation, this may not be considered a deficiency. If system modification is executed in accordance with Section 27, System Modifications, a recommendation can be made to improve an existing system in the appropriate section.
23.3 Circuit Fault Tolerance Test Sheet
NOTE 1 : Refer to Section 12 and 13
NOTE 2: Refer to Annex A, A3.86 for an explanation regarding the National Building Code (NBC) Fire Alarm (FA) Zone.
Circuit Fault Tolerance Test Sheet
| Building name : | TEST |  |  | Date (M/D/Y) : | 2025-01-12 |  | Page | ? | of | ?
Circuit fault test location |  | Type of fault (Record response time or indicate N/A) |  |  | Isolation results |  |  | Non-faulted circuit location
Identify Device Location where circuit fault was introduced and description of affected NBC Fire Alarm zone or area |  | Short | Open | Ground | Identify NBC Fire Alarm Zone or area Location where devices failed due to fault condition |  |  | Identify Individual Device tested for operation located in Non-Faulted NBC Fire Alarm zone or area |  |  | Pass or Fail

## 22.11 Signal Receiving Centre (hidden)
Section 22.11 Interconnection to the Fire Signal Receiving Centre
NOTE: If the fire alarm system DOES have an interconnections to a fire signal receiving centre, complete 22.11 for each transmitter.
There are no interconnections to a Fire Signal Receiving Centre on this system. .. |  | FALSE
A | The fire signal receiving centre transmitter is integral to the fire alarm control unit. | Yes | FALSE | No | FALSE | N/A | FALSE
B | Receipt of the alarm transmission to the fire signal receiving centre. | Yes |  | FALSE | No |  | FALSE
C | Receipt of the supervisory transmission to the fire signal receiving centre. | Yes | FALSE | No | FALSE | N/A | FALSE
D | Receipt of the trouble transmission to the fire signal receiving centre. | Yes |  | FALSE | No |  | FALSE
E | Disabling or disconnecting the fire signal receiving centre transmitter results in a specific trouble signal at the control unit or transmitter and also transmits a trouble signal to the fire signal receiving centre. | Yes |  | FALSE | No |  | FALSE
F | Disabling or disconnecting the fire signal receiving centre transmitter transmits a trouble signal to the fire signal receiving centre. | Yes |  | FALSE | No |  | FALSE
G | Record the company name and telephone number of the fire signal receiving centre. | Name:
Telephone:
H | Operation of the fire signal receiving centre disconnect means transmits trouble to the fire signal receiving centre. | Yes |  | FALSE | No |  | FALSE

## 33.5 SignallingDeviceSound (hidden)
Section 33.5 Signaling Device Sound Level Measurement
NOTE 1 : Refer to 23.2, 23.4, 27.1(f)
NOTE 2 : Device Legends and Notes are listed 33.1, Field Device Testing-Legend and Notes
Building Name: | TEST |  | Date (DD/MMM/YYYY): | 2025-01-12
Zone | Location | Ambient DBA | Alarm Signal DBA | Comments